### CENWP-OD-B																						19 June 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 24 of 2011, which covers the period from 12 through 18 June 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 480.9 to 501.3 kcfs.  Daily average project tailwater ranged from 31.5’ to 32.3’ msl.  Daily average powerhouse forebay elevation ranged from 72.7’ to 73.6’ msl.  Daily average river temperature was 58ºF all week. Secchi disk measurements ranged from 2.2’ to 2.5’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 279.6 to 303.3 kcfs.

  - Unit Operation.  Powerhouse One remains the priority powerhouse.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 15 went out of service at 0717 on 15 June for four year overhaul.

    - Unit 18 was out of service from 1006 until 1126 on 16 June to manually clean cooling water strainers.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.  This week required fish units to be placed on standby to float debris during daylight hours due to excessive drawdown.

  - Gatewell drawdowns are measured as needed and on Wednesdays.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS valves were closed this reporting week:

    - FV 3-7 was closed for cleaning from 0708 until 0718 on 13 June.

  - STS/VBS inspections.  No STS/VBS inspections occurred this reporting week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 27 June. |

  - Dewatering and Fish Salvage.  The following fish salvage activity occurred this reporting week.

    - Unit 15 was taken out of service for a 4 year overhaul on 16 June. Project biologists inspected the unit and found no fish.

- RESEARCH

  - Battelle - survival study.  Acoustic tagging and spring fish releases concluded.

  - CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.

  - NOAA - COE Walla Walla District transportation evaluation.  Sort by Code collections at the SMF continue.

  - NOAA/PSMFC - lamprey.  LPS count network remains installed.  Traps deployed at PH2 monoliths in tailrace and AFF.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues.  Fallbacks recorded crossing the separator bars:  7 steelhead, 13 salmon, and 15 unknown salmonids.  Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - WDFW - Fish Counting.  Visual counting continues.

  - USDA - Avian hazing. Hazing continues.

- FISHWAYS

  - Project biologists inspected 12 through 18 June.

  - Fish Passage Plan Observations.

- Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) – Nothing to report. |  |  |  |  |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| All week | PH2 entrances | Submergence <13’ | Necessary to maintain differential |  |  |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse 2 adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 6/12 | 57.6 | 57.1 |
| 6/13 | 57.6 | 57.1 |
| 6/14 | 57.1 | 57.6 |
| 6/15 | 57.0 | 57.4 |
| 6/16 | 56.8 | 57.2 |
| 6/17 | 56.8 | 57.2 |
| 6/18 | 56.6 | 57.0 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 18 June.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance. Due to high tailwater, water is flowing over the PH2 collection channel bulkheads.

    - SLEDs remain installed at all fishway entrances.  Most SLEDs are completely submerged due to high tailwater.

    - The AFF remains watered up.

    - Cascades Is. and Bradford Is. ladders were put into operation for shad passage on 14 June.

    - One section of diffuser grating between weir 34 and 35 came loose during high tailwater and was removed on 14 June.  Please see 16 June MOC for more information.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - All STSs are currently pulled.

    - The PH1 ice and trash sluiceway (ITS) remains in service.  Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon was turned off and removed as a precautionary measure against high tail water.

    - The B2CC remains in service.  Five avian lines are broken due to high tailwater and three remain.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  The CI LPS is in operation on weekdays.

    - The NDE ramp remains in the lowered position and is not currently operating.

    - WA Shore and Bradford Island LPSs remain watered up.

- CONSTRUCTION

  - PH1 Gantry 4.  New crane in August, 2011.

  - B2CC Hoist. Construction scheduled to begin fall of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 19 May requests that BON operate Powerhouse One as the priority powerhouse. Continue this operation until further notice. The goal of this operation is to minimize debris loading that is contributing to increased descaling and mortality of juvenile fish at Powerhouse Two (PH2). Additionally, operate units 14, 15, and 16 without Submersible Traveling Screens. Vertical Barrier Screens (VBSs) will remain installed for these units until debris loading causes a drawdown of 1.5 ft. Once VBSs satisfy this criterion, remove VBSs in units 14, 15, and 16. When selecting operating range within the 1% range of the PH2 screened units (12, 13, 17, and 18) make efforts to the extent practicable to achieve the following two objectives: 1) Do not exceed the 1.5 ft head differential prior to the next cleaning and 2) Maximize discharge at each unit. Objective 1 takes priority over objective 2.

  - A teletype sent on 03 June updated a former teletype requesting 100 kcfs spill from 10 April to 20 June for juvenile fish passage. The update clarifies that at no time is BON to voluntarily spill more than the fish passage spill cap on the revised TDG production estimate.

  - A teletype sent on 15 June requests summer spill for juvenile fish passage with two treatments of 85 kcfs during the day and 121 kcfs at night or 95 kcfs for 24 hours.  Effective 16 June at 0430 hours and continuing until 31 August at 2400 hours, spill in accordance with the 2011 Fish Passage Plan and the 2011 Summer Fish Operations Plan, Appendix E of the Fish Passage Plan.

  - A teletype sent on 17 June, effective as early as system conditions allow, requests that BON operate so that hourly averages are at or below 500 kcfs.

  - A teletype sent on 17 June requests that Bonneville pool be operated as follows:  Operate within a 1.5 foot band, soft constraint, from 0600 hours Monday, 20 June until 1800 hours Thursday, 23 June.  The goal of this operation is to limit pool fluctuation during treaty fishing.

JERRY CARROLL

Operations Project Manager