### CENWP-OD-B																						11 September 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 36 of 2011, which covers the period from 04 through 10 September 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 102.4 to 145.8 kcfs.  Daily average project tailwater ranged from 9.7’ to 13.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.5’ to 75.0’ msl.  Daily average river temperature ranged from 69 to 71ºF. Secchi disk measurements ranged from 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours.  Daily average spill ranged from 1.3 to 1.5 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 9 was out of service from 0933 until 1650 on 06 September for bearing repair. It went out of service at 0728 on 07 September due to bearing replacement.

    - Unit 10 was out of service from 0841 on 06 September until 0754 on 07 September for relay work.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 15 went out of service at 0719 on 05 September due to exciter failure.

    - Unit 16 went out of service at 0452 on 04 September due to exciter failure.

    - Unit 17 went out of service at 1010 on 09 August due to generator vibration.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

  - Dewatering and Fish Salvage. The following activity occurred this reporting week.

    - On 08 September Project Fisheries retrieved 2 sturgeon and 1 catfish from the Unit 9 draft tube. The fish were released at the Hamilton Island boat launch in good condition.

- RESEARCH

  - Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.

  - CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.

  - NOAA/PSMFC - lamprey.  LPS count network improvements moving forward.  Traps deployed at PH2 monoliths in tailrace and AFF.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Higher temperature sampling protocols were initiated at the beginning of the week when water temperatures exceeded 70ºF. Fallbacks recorded crossing the separator bars: 14 salmon, and 2 unknown salmonids. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - University of Idaho.  Tagging lamprey in the AFF continues.

  - University of Washington – JMF. A total of 25 juvenile shad were collected this week.

  - WDFW - Fish Counting.  Visual counting continues.

  - WDFW – Tule Counting. Tule counting began 17 August.

  - WDFW – AFF. Sampling for alternative gear study control group began 24 August.

  - Yakama Fisheries – AFF. Coho energy study began 22 August.

- FISHWAYS

  - Project biologists inspected 04 through 10 September.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 9/9 | B-branch entrance | Diff < 1.0’ | System in local | Ops adjusted |  |
| CASCADES ISLAND (CI) |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| All week | SDE, NDE | Will not lower past 3.5’ | Unknown, possible debris in gate slot | TR | 11-220488 |
| 9/9-10 | Weir 37 bleed off | Weir 37 staff gauge out of criteria | No electrical operation | TR | 11-247377 |
| All week | FV 6-9 | Valve not functioning in auto, Weir 67 staff gauge out of criteria | Unknown | TR | 11-234386 |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work has begun on replacing the PLC to allow for fully automated operation of the PH2 adult fishway.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average | AFF average | SMF Average |
| --- | --- | --- | --- | --- |
| 9/4 | 67.1 | 67.3 | 67.2 | 67.8 |
| 9/5 | 67.8 | 68.0 | 67.9 | 68.5 |
| 9/6 | 68.3 | 68.5 | 68.4 | 69.1 |
| 9/7 | 68.5 | 68.7 | 68.5 | 69.2 |
| 9/8 | 68.6 | 68.9 | 68.7 | 69.4 |
| 9/9 | 69.0 | 69.2 | 69.1 | 69.7 |
| 9/10 | 69.0 | 69.2 | 69.0 | 69.7 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 02 September.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs were removed from all entrance gates as of 05 July.

    - The AFF remains watered up.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon was returned to service on 06 July.

    - The B2CC was closed 01 September.  Five avian lines are broken due to high tailwater and three remain.

    - Spill ended on 1 September.

    - Truck releases of summer out-migrants originating from McNary began on 03 August. Truck releases from Lower Granite, Little Goose and Lower Monumental dams commenced on 17 August.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.  The CI LPS ceased 7 days a week operation on 09 September.

    - The NDE ramp remains in the lowered position.

    - WA Shore and Bradford Island LPSs remain watered up.

- CONSTRUCTION

  - PH1 Gantry 4.  Work has begun to remove the old crane. Once complete, the new crane will be delivered.

  - B2CC Hoist. Construction scheduled to begin fall of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 18 August requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5 foot band, hard constraint for periods and times, over the next three weeks. From 0600 hours Monday 22 August - 1800 hours Thursday, 25 August, 2011; from 0600 hours Tuesday 30 August – 1800 hours Friday, 02 September 2011; from 0600 hours Tuesday 06 September – 1800 hours Friday, 09 September 2011.

  - A teletype sent on 26 August requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5 foot band, hard constraint for the periods and times, over the next three weeks, as listed: From 0600 hours Monday 22 August – 1800 hours Thursday, 25 August 2011; from 0600 hours Monday 29 August – 1800 hours Friday, 02 September 2011; from 0600 hours Tuesday 06 September – 1800 hours Saturday, 10 September 2011.

  - A teletype sent on 26 August requests that on Saturday, 17 September, 2011 from 0800 to 1600 hours, BON forebay be maintained in a 1.5 foot band of 72.0 feet - 73.5 feet as a hard constraint. It is also requested as a soft constraint to maintain the BON pool in a 1 foot band of 72.0 feet -73.0 feet for the same date and times. This operation will assist a clean-up event at the mouth of the White Salmon river to remove abandoned boats and trash that could be washed downstream when Condit Dam is breached in late October.

  - A teletype sent on 29 August requests that on Monday, 5 September, outflows from the Bonneville and The Dalles be as low and constant as possible from 0600-1300 to allow for the cross channel swim at Hood River.

  - A teletype sent on 09 September requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5’ band, hard constraint from 0600 hours Monday 12 September – 1800 hours 16 September, 2011 during treaty fishing. Steady night time operations are most important (1900 through 0700 hours). A higher pool also facilitates the fishing operations.

  - A teletype sent on 09 September requests that The Dalles outflow be held as steady as possible from 0800 to 1100 Saturday, 10 September 2011. The steady flow is needed to ensure safe swimming conditions during the event located at the Riverfront park, approximately 2 miles downstream from The Dalles Dam. Recognizing the extremely late notification by the event coordinator, a preferred higher pool range at BON is not feasible under such short notice and due to the treaty fishing constraints. Any support from BPA to boost or keep BON pool elevation from dropping, while not impacted generation benefits or previously planned operations is kindly requested.

JERRY CARROLL

Operations Project Manager