### CENWP-OD-B																						09 October 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40 of 2011, which covers the period from 02 through 08 October 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 88.7 to 121.8 kcfs.  Daily average project tailwater ranged from 8.9’ to 11.3’ msl.  Daily average powerhouse forebay elevation ranged from 74.4’ to 75.0’ msl.  Daily average river temperature ranged from 64 to 66ºF. Secchi disk measurements remained unremitting at 7.0’ all week.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours per teletype in section 7.2.  Spill bay 18 remains on sill.  Daily average spill was 0.6 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 9 went out of service at 0728 on 07 September for bearing replacement.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 15 went out of service at 0719 on 05 September due to exciter failure.

    - Unit 16 went out of service at 0452 on 04 September due to exciter failure.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 and F2 were in reserve standby from 1357 until 1542 on 05 Oct. for a ROV inspection.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week:

    - FV1-1 was closed for cleaning from 0738 until 0800 on 03 Oct.

  - STS/VBS inspections.  The following STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 10/03 | 822 | OK |
| 13 | 10/03 | 822 | OK |
| 14 | 10/03 | 146 | OK |
| 15 | 10/03 | 94 | OK |
| 16 | 10/03 | 162 | OK |
| 17 | 10/03 | 825 | OK |
| 18 | 10/03 | 825 | OK |

  - Dewatering and Fish Salvage. The following activities occurred this reporting week.

    - On 05 October Project Fisheries personnel salvaged 3 Pacific Lamprey when dewatering B-branch entrance below tailwater in association with the emergency B-branch repairs. Fish were released into the forebay in good condition.

    - On 04 October Project Fisheries personnel with assistance from District Fisheries salvaged 25 White Sturgeon and 3 Channel Catfish from Unit 15 draft tube. Fish were released at the Hamilton Island boat launch.

- RESEARCH

  - Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.

  - CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF continues.

  - CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.

  - NOAA/PSMFC - lamprey.  LPS count network improvements moving forward. Cascades Island LPS trap and haul concluded on 15 September.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Fallbacks recorded crossing the separator bars: 9 salmon, and 9 unknown salmonids. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - University of Idaho.  Tagging lamprey in the AFF concluded in early September.

  - University of Washington – JMF. A total of 25 juvenile shad were collected this week..

  - WDFW - Fish Counting.  Visual counting continues.

  - WDFW – Tule Counting. Tule counting concluded 03 October.

  - WDFW – AFF. Sampling for alternative gear study control group began 24 August.

- FISHWAYS

  - Project biologists inspected 02 through 08 October.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 10/2, 8 | A-branch staff gauge | Water level > 1.1’ | B-branch OOS | N/A |  |
| All week | BI staff gauge | Water level < 0.9’ | B-branch OOS | N/A |  |
| All week | B-branch dewatered |  | Emergency repairs | N/A |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| 10/4 | Weir 37 bleed off | Weir 37 staff gauge out of criteria | No electrical operation | TR | 11-247377 |

    - PH1 PCC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work replacing the PLC to allow for fully automated operation of the PH2 adult fishway is complete but some testing and adjustments are ongoing.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average* | AFF average | SMF Average |
| --- | --- | --- | --- | --- |
| 10/02 | 64.4 | 64.6 | 64.5 | 65.2 |
| 10/03 | 64.3 | 64.5 | 64.4 | 65.1 |
| 10/04 | 64.2 | 64.4 | 64.3 | 65.0 |
| 10/05 | 63.8 | 64.1 | 64.0 | 64.7 |
| 10/06 | 63.2 | 63.4 | 63.3 | 64.0 |
| 10/07 | 62.2 | 62.5 | 62.4 | 63.1 |
| 10/08 | 62.0 | 62.2 | 62.1 | 62.8 |

* Bradford Island B-branch was dewatered on 17 September.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 07 October.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs were removed from all entrance gates as of 05 July.

    - The AFF remains watered up.

    - B-branch was dewatered on 17 September. It remains out of service. See section 7.1 and MFR 110919 BON B-branch emergency dewater for more information.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon was returned to service on 06 July.

    - The B2CC was closed 01 September.  All B2CC avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled once repairs are complete.

    - Spill ended on 01 September.

    - Truck releases of summer out-migrants originating from McNary began on 03 August. Truck releases from Lower Granite, Little Goose and Lower Monumental dams commenced on 17 August.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The CI LPS was taken out of service for the season on 15 September.

    - The NDE ramp is out of service for the season.

    - WA Shore and Bradford Island LPSs remain watered up.

- CONSTRUCTION

  - PH1 Gantry 4. Testing of the new crane continues.

  - B2CC Hoist. Construction scheduled to begin fall of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent 16 September states that emergency repair at the B branch Bradford Island fish ladder entrance is required immediately due to structural integrity issues and a high risk of failure related to erosion. The B branch needs to be dewatered and repaired. This Saturday in the morning, both A and B branch will be out of service in order to install concrete orifice blocks in B branch just below the junction pool. Once installed, the A branch will be reopened. Effective immediately and until the fish biologists notify the control room operator operate Powerhouse 2 as priority and then use Powerhouse 1 if additional generation is requested by BPA. Continue with the same unit priority as listed in the 2011 Fish Passage Plan. It is recognized that due to the current high number of adult returning fish the project has been in a split flow unit priority, following the 2011 Fish Passage Plan guidance. Once notified by the biologists, return to this priority unless instructed differently by RCC. Effective immediately stop all attraction flow spill from spillbay 18 and add the same volume on to spill at spillbay 1. Continue this operation until further notice, even after switching back to the split flow gen pattern. The purpose of this operation is to ensure better attraction to the Cascades Island entrance.

  - A teletype sent on 19 September states that effective immediately and until further notice from project biologists or RCC, operate Powerhouse 2 as the priority powerhouse in accordance with the 2011 Fish Passage Plan table BON-14. Fish passage numbers have decreased below 20,000 adult salmonids per day; therefore split flows are no longer required. Until further notice, close spillbay 18 and spill attraction flow only through spillbay 1. Consistent with the FPP, open spillbay 1 spill gate 6” to provide attraction flow to the Cascades Island ladder during daylight hours of 0600 to 1930. Until further notice, operate the BON forebay to not exceed an elevation of 75.5’, hard constraint.

  - A teletype sent on 27 September states that, effective immediately operate attraction flow consistent with the 2011 FPP. Specifically, operate spillbay 1 spill gate with an opening of 6 inches. Keep spill gate 18 closed since B-branch is out of service. Continue to operate Powerhouse 1 at 1%. In the event hydraulic capacity would cause BON to spill then pick up generation at PH1 to best geometry (1.3 to 1.5 kcfs above the current 1% range) prior to spilling at BON. The intent of operation PH1 at best geometry would be in an effort to minimize spilling at BON once all units have been fully loaded. Once spilling at BON is no longer a concern then revert back to the 1% operation range. Should spill occur at BON then spill in accordance with the spill pattern titled “Special Spill Pattern for North End Spill Bays 1-9”.

  - A teletype sent on 30 September requests that BON pool be operated as follows for treaty fishing: Operate within a 1.5’ band, hard constraint for the period and times listed: From 0600 hours Monday, 03 October, to 1800 hours Thursday, 06 October 2011.

  - A teletype sent on 05 October requests that from 0630 hours on 06 October to 1800 hours 31 October 2011, BPA notify the BON operator and RCC at least 30 minutes, or more, prior to any spill at BON. When notified, BON will take appropriate steps to evacuate workers from the spillway tailrace. When workers are not present, notice may allow the contractor to better secure and monitor equipment in the tailrace before and during spill.

  - A teletype sent on 07 October states that effective at 0700 hours on Tuesday, 11 October, until further notice, change powerhouse priority to PH1. Operate according to the 2011 FPP table BON-14 for “Second Powerhouse Adult Fish Ladder Out of Service”. Concurrent with the above operation, operate PH1 turbine units to Best Geometry, expanding the upper limit of the 1% operating range up to 11.7 kcfs per unit. These operations are necessary to reduce flow to PH2 to minimize attraction flow at Washington Shore fish ladder.

  - A teletype sent on 07 October requests that best effort be made as a soft constraint to maintain BON tailwater below elevation 9’ from 0900 to 1500 hours on the following days: Monday, 10 October 2011, and Tuesday, 11 October 2011. The low tailwater elevations assist in cement pours on Tuesday in connection with the repair of erosion below the B-branch Bradford Island ladder.

JERRY CARROLL

Operations Project Manager