### CENWP-OD-B																						13 November 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 45 of 2011, which covers the period from 06 through 12 November 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 122.5 to 133.4 kcfs.  Daily average project tailwater ranged from 11.5’ to 12.5’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 74.2’ msl.  Daily average river temperature ranged from 54 to 56ºF. Secchi disk measurements ranged from 5.0’ to 6.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 was moved to 12” open during daylight hours per teletype in section 7.2.3.  Spill bay 18 remains on sill.  Daily average spill ranged from 1.9 to 25.8 kcfs.

  - Unit Operation.  Powerhouse One remains the priority powerhouse.

    - Unit 8 went out of service at 1040 on 05 November due to an emergency trip related to an exciter problem. It was returned to service at 1508 on 10 November.

    - Unit 10 was out of service from 1342 until 1550 on 09 November for trash raking.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 15 went out of service at 0719 on 05 September 2011 due to exciter failure.

    - Unit 16 went out of service at 0452 on 04 September 2011 due to exciter failure.

    - Unit 18 was out of service from 1111 until 1610 on 08 November for a ROV fish unit trashrack inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 went out of service at 0003 on 14 October 2011 for WA shore maintenance.

    - F2 went out of service at 0005 on 14 October 2011 for WA shore maintenance.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | STSs removed. |

  - Dewatering and Fish Salvage. The following activities occurred this reporting week.

    - On 08 November Project Fisheries salvaged 5 coho, 1 steelhead, 1 lamprey, 1 shad, 1 sculpin, and 1 juvenile sturgeon from the north monolith. The fish were released into the forebay in good condition.

- RESEARCH

  - Battelle - survival study.  Monitoring University of Idaho acoustic tagged adult lamprey.

  - CRITFC - Sea lion.  Acoustic receivers for sea lion tags remain anchored in the BRZ.

  - NOAA/PSMFC - lamprey.  LPS count network improvements moving forward.

  - WDFW - Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 06 through 12 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/6-8 | A-branch staff gauge | Water level > 1.1’ | B-branch OOS | N/A |  |
| All week | BI staff gauge | Water level < 0.9’ | B-branch OOS | N/A |  |
| All week | B-branch dewatered |  | Emergency repairs | N/A |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| All week | Ladder dewatered from UMT confluence “Y” junction to TW |  | Emergency repairs | N/A |  |
| All week | DSM2 dewatered |  | Emergency WA shore repairs | N/A |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work replacing the PLC to allow for fully automated operation of the PH2 adult fishway is complete but some testing and adjustments are ongoing.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 11/06 | 54.3 | 54.5 |
| 11/07 | 54.2 | 54.4 |
| 11/08 | 53.9 | 54.1 |
| 11/09 | 53.7 | 54.0 |
| 11/10 | 53.4 | 53.6 |
| 11/11 | 52.9 | 53.1 |
| 11/12 | 52.4 | 52.6 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on Veterans Day, 11 November.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs were removed from all entrance gates as of 05 July.

    - B-branch remains out of service.

    - The AFF remains out of service for WA shore repairs.

    - WA shore ladder remains out of service below the “Y” junction (UMT confluence) in facilitation of diffuser grating and AWS repairs.

    - The south monolith at PH2 was dewatered on 20 October, and the north monolith was dewatered on 08 November to facilitate repairs on diffusers and debris removal in the AWS.

  - Juvenile Fishways.

    - DSM2 was dewatered on 03 November. Submersible Traveling Screens (STSs) were all removed by 02 November.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains winterized.

    - The B2CC remains closed.  All B2CC and Cascades Island avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled once repairs are complete.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The CI LPS remains out of service for the season.

    - The NDE ramp remains out of service for the season.

    - WA Shore and Bradford Island LPSs were taken out of service on 09 November.

- CONSTRUCTION

  - B2CC Hoist. Construction scheduled to begin winter of 2011.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 31 October states, effective 01 November operate BON tailwater to provide adequate spawning conditions for Chum salmon. Hard constraint 1: Maintain tailwater at a minimum of 11.3’ all hours. Hard constraint 2: Maintain tailwater within 0.7’ band of 11.3’-12.0’ daily from 0630-1700 hours.

  - A teletype sent on 07 November requests that from 1600 hours to 1700 hours on 08 November operate BON pool as high as possible, up to 75.5’. This request is made to help free a stuck lumber barge located near Bingen.

  - A teletype sent on 10 November updated and replaced previous teletypes concerning forebay range, PH priority, and spill operations.

    - Continue to operate BON forebay in the 73.0-75.5’ range during daytime hours. FV 3-9 may be operated to provide additional water to A-branch as necessary.

    - Continue to operate PH1 as the priority powerhouse, and operate the units up to the cavitation limit.

    - Continue to open spill bay 1 12” during daytime hours to provide additional attraction flow to Cascades Island. Keep spill bay 18 on sill.

    - Effective immediately until 1700 hours on 13 November spill flows in excess of PH1 capacity with the spill pattern titled “Special Spill Pattern for North End Spill Bays 1-9” up to 70 kcfs during daytime hours. Operate PH2 units for flows in excess of PH1 capacity during nighttime hours. After 1700 hours on 13 November operate PH2 units for flows in excess of PH1 capacity for all hours.

JERRY CARROLL

Operations Project Manager