### CENWP-OD-B																						27 November 2011

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 47 of 2011, which covers the period from 20 through 26 November 2011.

- OPERATION SUMMARY

  - Daily average river flows ranged from 124.0 to 145.7 kcfs.  Daily average project tailwater ranged from 12.6’ to 14.5’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 74.2’ msl.  Daily average river temperature ranged from 48 to 50ºF. Secchi disk measurements ranged from 4.5’ to 6.5’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 remains 12” open during daylight hours.  Spill bay 18 remains on sill.  Daily average spill  was 1.0 kcfs.

  - Unit Operation.  Powerhouse One remains the priority powerhouse.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 13 was out of service from 0004 on 21 November 2011 until 1429 on 23 November 2011 for servo leak repair.

    - Unit 16 went out of service at 0452 on 04 September 2011 due to exciter failure.

    - Unit 18 went out of service at 1030 on 23 November 2011 due to water in the thrust bearing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 went out of service at 0003 on 14 October 2011 for WA shore maintenance.

    - F2 went out of service at 0005 on 14 October 2011 for WA shore maintenance.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed for cleaning from 1113 until 1124 on 23 November.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | STSs removed. |

  - Dewatering and Fish Salvage. No fish salvage activities occurred this reporting week.

- RESEARCH

  - WDFW - Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 20 through 26 November. NOAA Fisheries inspected 25 November.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |
| 11/23-24 | A-branch staff gauge | Water level > 1.1’ | B-branch OOS | N/A |  |
| All week | BI staff gauge | Water level < 0.9’ | B-branch OOS | N/A |  |
| All week | B-branch dewatered |  | Emergency repairs | N/A |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |  |
| All week | Ladder dewatered from UMT confluence “Y” junction to TW |  | Emergency repairs | N/A |  |
| All week | DSM2 dewatered |  | Emergency WA shore repairs | N/A |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs scheduled for 2011/2012 in water work period.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

    - The SA-24 board that controls the Powerhouse Two adult ladder components is in need of replacement. Work replacing the PLC to allow for fully automated operation of the PH2 adult fishway is complete but some testing and adjustments are ongoing.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

Table 3.  Bonneville Fishway Temperatures

| Date | WA. Shore average | BI average |
| --- | --- | --- |
| 11/20 | 48.4 | 48.7 |
| 11/21 | 48.0 | 48.3 |
| 11/22 | 47.8 | 48.1 |
| 11/23 | 47.5 | 47.9 |
| 11/24 | 47.4 | 47.7 |
| 11/25 | 47.3 | 47.5 |
| 11/26 | 47.1 | 47.3 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 25 November.

    - 10 of 12 floating orifice gates (FOGs) are installed with sea lion barriers in place.  Two gates remain out for maintenance.

    - SLEDs were removed from all entrance gates as of 05 July.

    - B-branch remains out of service.

    - The AFF remains out of service for WA shore repairs.

    - WA shore ladder remains out of service below the “Y” junction (UMT confluence) in facilitation of diffuser grating and AWS repairs.

  - Juvenile Fishways.

    - DSM2 remains out of service. STSs are removed.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains winterized.

    - The B2CC remains closed.  All B2CC and Cascades Island avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled once repairs are complete.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPS systems remain out of service for the season.

- CONSTRUCTION

  - B2CC Hoist. Construction continues.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 23 Nov. replaces a previous teletype for operation of BON tailwater to provide adequate spawning conditions for Chum salmon. Hard constraint 1: Maintain tailwater at a minimum of 11.7’ all hours. Hard constraint 2: Maintain tailwater within 0.8’ band of 11.7’-12.5’ daily from 0600-1700 hours.

  - A teletype sent on 23 Nov. states in order to keep the latest established Bon tailwater flow range for chum, total project flow may be decreased to as low as 58 kcfs as long as the estimated flow at the confluence of the Columbia and Willamette rivers is equal to or exceeds 77 kcfs.  The 58 kcfs and 77 kcfs is a hard constraint navigation requirement.

  - A teletype sent on 23 November updated and replaced previous teletypes concerning forebay operating range, PH1 priority, and updated operation of spillway and PH2.

    - Continue to operate BON forebay in the 73.0-75.5’ range during daytime hours. FV 3-9 may be operated to provide additional water to A-branch as necessary.

    - Continue to operate PH1 as the priority powerhouse, and operate the units up to the cavitation limit.

    - Continue to open spill bay 1 12” during daytime hours to provide additional attraction flow to Cascades Island. Keep spill bay 18 on sill.

    - Effective immediately until further notice, during all hours pass flow in excess of PH1 capacity through available PH2 units as necessary according to the following unit priority order:  12,13,14,16,17,18,15.  Unit 15 will be on a last on, first off basis until the project can resolve issues associated with results from the last heat test performed on 17-19 Nov. that indicated the unit is operating near one of the heat limits.

JERRY CARROLL

Operations Project Manager