### CENWP-OD-B																						26 February 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 08 of 2012, which covers the period from 19 through 25 February 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 129.4 to 201.3 kcfs.  Daily average project tailwater ranged from 12.3’ to 17.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.4’ to 75.3’ msl.  Daily average river temperature ranged from at 38 to 40ºF. Secchi disk measurements ranged from 4.0’ to 7.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 remains 6” open during daylight hours.  Spill bay 18 remained on sill due to B-branch dewatering until 22 February when B-branch was returned to service.  Daily average spill ranged from 0.6 to 1.1 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0715 until 0917 on 21 February for STS installation.

    - Unit 13 was out of service from 0921 until 1336 on 21 February for STS installation.

    - Unit 14 was out of service from 1339 until 1620 on 21 February for STS installation.

    - Unit 15 was out of service from 0700 until 0940 on 22 February for STS installation.

    - Unit 16 went out of service at 0452 on 04 September 2011 due to exciter failure.

    - Unit 17 was out of service from 1127 until 1404 on 22 February for STS installation.

    - Unit 18 went out of service at 1030 on 23 November 2011 for a 4 year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | STSs installed week of 19 February. |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - WDFW - Fish Counting.  Video counting continues.

  - PNNL/Battelle. Surgeon/tagging training and fish condition research at the JMF scheduled to begin week of 26 February.

- FISHWAYS

  - Project biologists inspected 21, 22, and 23 February.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) – Dewatered. |  |  |  |  |  |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |  |
| WASHINGTON SHORE (WS) – Nothing to report. |  |  |  |  |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 23 February.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance. Stab plates were installed on 07 and 08 December in accordance with the FPP for 1 Fish Unit operations.

    - All SLEDs are installed.

    - Bradford Island ladders (A and B branch) were returned to service on 22 February.

    - The AFF remains dewatered.

    - WA shore ladder remains in service.

  - Juvenile Fishways.

    - DSM2 was returned to service on 14 February. The switch gate at the JMF remains in bypass.

    - STSs were installed the week of 19 February.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains winterized.

    - The B2CC remains closed.

    - All B2CC and Cascades Island avian lines were removed to facilitate barge access for B-branch emergency repairs. They will be reinstalled as soon as maintenance schedules allow.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPS systems remain out of service for the season.

- CONSTRUCTION

  - B2CC Hoist. Construction continues.

  - Spillway Debris Removal. Scheduled to commence on 02 March.

  - Seawater Recirculation System Removal (JMF). Scheduled to commence on 05 March.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 23 November states in order to keep the latest established Bon tailwater flow range for chum, total project flow may be decreased to as low as 58 kcfs as long as the estimated flow at the confluence of the Columbia and Willamette rivers is equal to or exceeds 77 kcfs.  The 58 kcfs and 77 kcfs is a hard constraint navigation requirement.

  - A teletype sent on 28 December replaces a previous teletype for operation of BON tailwater to provide adequate spawning conditions for Chum salmon. As a hard constraint, maintain tailwater at a minimum of 12.0’ all hours.

  - A teletype sent on 19 January states that, effective immediately and until further notice, operate BON to minimize spill until the project removes boulders that have accumulated in the spillway stilling basin. Operate turbine units above the 1% of the best efficiency range as necessary to pass flows. The project is authorized to operate up to the maximum load within the cavitation limit. If flows exceed hydraulic capacity, operate the spillway as necessary according to the spill pattern defined in “BON Special Spill Pattern – Jan. 19, 2012”.

  - A teletype sent on 24 February states that, effective at 1000 hours on 27 February, through 1800 hours on 31 March, BPA is requested to provide at least one-hour notification to BON control room prior to spill. A day-ahead advisory of possible spill is also requested, when possible, in order to inform the contractor at the site of possible events and evacuations of the stilling basin work area.

JERRY CARROLL

Operations Project Manager