### CENWP-OD-B																						15 April 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 15 of 2012, which covers the period from 08 through 14 April 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 258.9 to 326.8 kcfs.  Daily average project tailwater ranged from 21.3’ to 24.6’ msl.  Daily average powerhouse forebay elevation ranged from 72.2’ to 74.2’ msl.  Daily average river temperature ranged from 45 to 46ºF. Secchi disk measurements ranged from 2.0’ to 2.8’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bays remain 6” open during daylight hours. Daily average spill ranged from 81.6 to 115.1 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 3 was out of service from 0853 until1010 on 12 April for black start testing.

    - Unit 4 was out of service from 0855 until1012 on 12 April for black start testing.

    - Unit 9 was out of service from 1058 until 1118 on 12 April to disconnect well monitoring equipment.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0844 until 1448 on 09 April for WECC testing. Unit 12 was also out of service from 0720 until 1554 on 11 April for the MU11 tail log dive.

    - Unit 13 was out of service from 1452 until 1803 on 09 April, and from 0805 until 0948 on 10 April for WECC testing.

    - Unit 14 was out of service from 0950 until 1534 on 10 April for WECC testing.

    - Unit 15 was out of service from 1643 until 1733 on 10 April, and from 0820 until 1118 on 11 April for WECC testing.

    - Unit 16 was out of service from 1212 until 1629 on 11 April for WECC testing.

    - Unit 17 was out of service from 1638 until 1725 on 11 April, and from 0817 until 1052 on 12 April for WECC testing.

    - Unit 18 was out of service from 1541 on 10 April until 1652 on 11 April for an oil leak inspection. Unit 18 was out of service from 1125 until 1627 on 12 April for WECC testing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - Fish Unit 1 was out of service from 0305 until 1608 on 11 April for the MU11 tail log dive.

    - Fish Unit 2 was out of service from 0305 until 1612 on 11 April for the MU11 tail log dive.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed to float trash from 0015 until 0045 on 10 April, from 0120 until 0155 on 11 April, and from 0117 until 0148 on 12 April.

    - FV 3-7 was closed for cleaning from 1545 until 1551 on 12 April.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12 | 04/11 | Unknown | OK, STSs were operable but Run Hours counter was broken. TR’d and repaired. |
| 13 | 04/11 | 1467 | OK |
| 14 | 04/11 | 1381 | OK |
| 15 | 04/11 | 1166 | OK |
| 16 | 04/11 | 892 | OK |
| 17 | 04/11 | 1353 | OK |
| 18 | 04/11 | 1139 | OK |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - Battelle - survival study.  Surgeon/tagging training and fish condition research continue at the JMF. Fish for training currently held in raceways at the SMF. Hydrophone installation completed on 21 March.

  - CRITFC - Sea lion hazing.  Hazing continues.

  - FFU - Sea lion.  Observations continue. Weekly pinniped reports can be found at: http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2012/sea_lion_hazing2012.html

  - NOAA - lamprey. Personnel moved the lamprey trap davit at the South Monolith SDE closer to the entrance allowing the trap to sit adjacent to attraction flow.

  - ODFW/WDFW - Sea lion. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Acoustic tagging and branding began on 06 February. NOAA Fisheries authorized permanent removal of specific California sea lions effective 20 March.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring began on 01 March. Sort by Code is active. Fallbacks recorded crossing the separator bars this week: 10 steelhead. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm. Spring Creek fish arrived at BON at approximately 0040 on 12 April. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - USDA - Sea lion hazing. Hazing continues.

  - WDFW - Fish Counting.  Visual counting continues.

- FISHWAYS

  - Project biologists inspected 08 through 14 April.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| SPILLWAY |  |  |  |  |
| 04/11-14 | Bay 2 and 17 | Incorrect spill pattern | Failed hoists | Under repair |
| BRADFORD ISLAND (BI) |  |  |  |  |
| 04/10 | ITS | Closed | Log removal | RTS on 04/11 |
| 04/09 | PH1CC | N and S differentials > 2.0’ | Weir gate malfunction | None |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |
| All week | PH2 Entrances | Gates < 13’ submergence | Unknown | Investigation |
| 04/11 | PH2 Entrances | No differential | MU11 dive ops | None |
| 04/11-13 | Weir 38 | Water level < 0.9’ | Unknown | Adjusted Valve #2 |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November. Temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 07 April.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance. Sea lion barriers are in place on all installed FOGs.

    - All SLEDs are installed.

    - All ladders remain in service.

    - The AFF was watered-up on 11 April.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC was opened on 19 March upon reaching the kelt trigger.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPS systems remain out of service for the season.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 23 November states in order to keep the latest established Bon tailwater flow range for chum, total project flow may be decreased to as low as 58 kcfs as long as the estimated flow at the confluence of the Columbia and Willamette rivers is equal to or exceeds 77 kcfs.  The 58 kcfs and 77 kcfs is a hard constraint navigation requirement.

  - A teletype sent on 28 December replaces a previous teletype for operation of BON tailwater to provide adequate spawning conditions for Chum salmon. As a hard constraint, maintain tailwater at a minimum of 12.0’ all hours.

  - A teletype sent on 06 April requests that, as a soft constraint, the BON forebay be at or below elevation 72.5’ from 1200 until 1500 hours on 09 April. The requested operation assists contractors welding together 15 steel pilings to from three dolphins for the city of The Dalles.

  - A teletype sent on 09 April states that, effective from 0001 hours on 10 April until 2400 hours on 15 June, operate in accordance with the 2012 Fish Operations Plan to provide spill for juvenile fish passage during the spring season at BON, as follows: 100 kcfs for 24 hours per day following the spill pattern defined in the 2012 Fish Passage Plan.

  - A teletype sent on 10 April requests that, effective immediately, the project operate to achieve a forebay elevation of 75.0-76.5’ as soon as practicable, and maintain the forebay elevation within the 1.5’ band as a soft constraint through 1200 hours on 11 April. This operation is intended to facilitate the removal of a large tree that has become lodged in the PH1 ITS.

  - A teletype sent on 13 April states that, effective immediately and extending through 1700 hours on 18 April, operate PH2 units at 25% of the 1% operating range while maintaining spring spill rates. This operation is intended to improve passage conditions through the PH2 gatewells during the downstream migration of approximately 8 million juvenile chinook released from Spring Creek Nation Fish Hatchery on 11 and 13 April.

  - A teletype sent on 13 April updates the spill priority list order for Fish Passage Season for the Columbia Basin projects with associated total dissolved gas spill caps.

JERRY CARROLL

Operations Project Manager