### CENWP-OD-B																						29 April 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 17 of 2012, which covers the period from 22 through 28 April 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 332.6 to 442.1 kcfs.  Daily average project tailwater ranged from 24.6’ to 29.6’ msl.  Daily average powerhouse forebay elevation ranged from 72.5’ to 74.9’ msl.  Daily average river temperature ranged from 48 to 51ºF. Secchi disk measurements ranged from 2.0’ to 4.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively, and remain at least 6” open during daylight hours. Daily average spill ranged from 106.0 to 229.1 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 5 was out of service from 1429 until 1550 on 24 April due to loss of Atlas Communication.

    - Unit 11 has remained out of service since 12 June 2008 due to rotor damage.

    - Unit 12 was out of service from 0703 until 0834 on 25 April for a ROV inspection of Unit 11 tail logs.

    - Unit 13 was out of service from 0703 until 0831 on 25 April for a ROV inspection of Unit 11 tail logs.

    - Unit 18 was out of service from 1903 until 1956 on 27 April due to a cooling water strainer clog.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - Fish Units 1 and 2 were both reduced to low flow from 0703 until 0834 on 25 April to reduce flow from the FOGs to allow for a ROV inspection of Unit 11 tail logs.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed to float trash from 0300 until 0500 on 23 April, from 0001 until 0430 on 24 April, from 0005 until 0330 on 25 April, and from 2140 until 2320 on 25 April.

    - FV 3-7 was closed for cleaning from 0708 until 0814 on 23 April and closed for floating trash from 0005 until 0330 on 25 April.

    - FV 3-9 was closed for cleaning from 0708 until 0814 on 23 April.

    - FV 6-9 was closed for cleaning from 1055 until 1115 on 27 April.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | NA | OOS | U11 remains out of service. |
| 12-18 | NA | NA | Inspection scheduled for week of 08 April |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - Battelle – Surgeon Training/Assessment. Surgeon/tagging training at the JMF concluded 27 April. Fish for training were held in raceways at the JMF. Surgeon assessment and Sort-By-Code activities will continue through July.

  - Battelle - Survival Study. Hydrophone installation completed on 21 March.

  - CRITFC – AFF.  Annual chinook, coho, sockeye and steelhead sampling in the AFF began 23 April.

  - CRITFC - Sea Lion Hazing.  Hazing continues.

  - FFU - Sea Lion.  Observations continue. Weekly pinniped reports can be found at: http://www.nwd-wc.usace.army.mil/tmt/documents/fish/2012/sea_lion_hazing2012.html

  - NOAA – Juvenile Steelhead. Barged and in-river migrant sampling scheduled to begin in May.

  - NOAA - Lamprey. Personnel moved the lamprey trap davit at the South Monolith SDE closer to the entrance allowing the trap to sit adjacent to attraction flow.

  - NOAA – Pathology. 25 yearling Chinook were collected at the JMF for research this week.

  - ODFW – NPMP. Sampling in the BRZ occurred on 25 April.

  - ODFW/WDFW - Sea lion. Sea lion traps remain adjacent to the B2CC and downstream of the old Navlock.  Acoustic tagging and branding began on 06 February. NOAA Fisheries authorized permanent removal of specific California sea lions effective 20 March.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring began on 01 March. Sort by Code is active. Fallbacks recorded crossing the separator bars this week: 42 steelhead, 2 salmon, and 8 unknown salmonids. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - USDA - Sea Lion/Avian hazing. Hazing continues.

  - WDFW - Fish Counting.  Visual counting continues.

- FISHWAYS

  - Project biologists inspected 22 through 28 April.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| SPILLWAY |  |  |  |  |
| All week | Bay 17 | Incorrect height for spill pattern | Failed hoists | Under repair |
| BRADFORD ISLAND (BI) – Nothing to report. |  |  |  |  |
| 04/25 | PH1CC, S-DIFF | Diff < 1.0’ | Unknown | N/A |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |
| All week | PH2 Entrances | Gates < 13’ submergence | Necessary to maintain differential | N/A |
| 04/25 | PH2 Entrances | No Differential | ROV on U11 tail logs | RTS |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November. Temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 28 April.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance. Sea lion barriers are in place on all installed FOGs.

    - All SLEDs are installed.

    - All ladders remain in service.

    - The AFF remains in bypass.

  - Juvenile Fishways.

    - DSM2 remains in service.

      - High water levels caused by debris in the DSM2 channel caused the ERG to trip on 26 April. The result was a temporary loss of water to the 2-mile pipe and a sample interruption at the JMF from 1515-1605.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC remains open.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPS systems remain out of service for the season.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 23 November states in order to keep the latest established Bon tailwater flow range for chum, total project flow may be decreased to as low as 58 kcfs as long as the estimated flow at the confluence of the Columbia and Willamette rivers is equal to or exceeds 77 kcfs.  The 58 kcfs and 77 kcfs is a hard constraint navigation requirement.

  - A teletype sent on 28 December replaces a previous teletype for operation of BON tailwater to provide adequate spawning conditions for Chum salmon. As a hard constraint, maintain tailwater at a minimum of 12.0’ all hours.

  - A teletype sent on 09 April states that, effective from 0001 hours on 10 April until 2400 hours on 15 June, operate in accordance with the 2012 Fish Operations Plan to provide spill for juvenile fish passage during the spring season at BON, as follows: 100 kcfs for 24 hours per day following the spill pattern defined in the 2012 Fish Passage Plan. This teletype was updated on 20 April to define minimum generation requirements.

  - A teletype sent on 25 April states that a 24-hour tailwater fluctuation range of up to 5.0’ is authorized at BON from 0700, 25 April to 0700, 26 April. Bonneville OPM Jerry Carroll approved this exceedance of the normal 24-hour tailwater fluctuation limit of 4.0’ in response to expected increasing inflows and ongoing flood control.

  - A teletype sent on 26 April states that, effective immediately for the purposes of system flood control; make best efforts to maintain outflows from BON, for a daily average, between 410 kcfs with max instantaneous of 430 kcfs, through 2400 hours, 30 April.

  - A teletype sent on 27 April states that, effective from 1700 hours on 30 April and extending through 1700 hours on 04 May, operate PH1 units up to the upper limit (100%) of the 1% operating range and all PH2 units up to the mid-point (50%) of the 1% operating range. This operation is intended to improve passage conditions during the downstream migration of approximately 4 million juvenile chinook released from Spring Creek Nation Fish Hatchery on 30 April.

  - A teletype sent on 25 April updates the spill priority list order for Fish Passage Season for BON with associated total dissolved gas spill caps.

JERRY CARROLL

Operations Project Manager