### CENWP-OD-B																						15 July 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 28 of 2012, which covers the period from 08 through 14 July 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 319.7 to 343.5 kcfs.  Daily average project tailwater ranged from 23.8 to 24.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.6’ msl.  Daily average river temperature ranged from 62 to 66ºF. Secchi disk measurements ranged from 4.5’ to 6.0’.

  - Summer Spill for fish passage is in effect. Daily average spill ranged from 115.7 to 155.1 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse.

    - Unit 10 went out of service at 0928 on 09 July for a 5 year overhaul.

    - Unit 11 went out of service at 0005 on 06 July for governor trouble.

    - Unit 14 went out of service at 0710 on 11 June for a 4 year overhaul.

    - Unit 18 was out of service from 0006 on 09 July until 1623 on 12 July for a headgate swap.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - Fish Unit 1 went out of service at 0156 on 06 July for a servo oil leak. The unit was returned to service at 2019 on 13 July.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | STSs from Units 13-17 scheduled for removal starting 25 July |

  - Dewatering and Fish Salvage. The following dewatering or fish salvage activities occurred this week.

    - On 09 July Project Biologists recovered 50 subyearling Chinook and 5 mini-jacks from the Unit 10 headgates. Additionally, 600 subyearling Chinook, 15 American Shad, and 30 Chinook mini-jacks were recovered from the Unit 10 scroll case. All fishes were released at Hamilton Island boat launch.

    - On 10 July Project Biologists recovered 15 White Sturgeon, 30 Pacific Lamprey, and 20 subyearling Chinook from the Unit 10 draft tube. All fishes were released upstream at the Navlock.

- RESEARCH

  - Battelle/PNNL – Surgeon Training/Assessment. Surgeon assessment and Sort-By-Code activities will continue through July.

  - Battelle/PNNL - Survival Study. Hydrophones remain installed.

  - CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF continues.

  - NOAA - Lamprey. LPS count network installed. Trapping at the CI LCS, WA shore NDE, and the AFF continues.

  - NOAA – Pathology. 25 subyearling Chinook were collected at the JMF for research this week.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Sort by Code is active for PNNL. Fallbacks recorded crossing the separator bars this week: 17 steelhead, 12 salmon, and 4 unknown salmonids. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm. Gas Bubble Trauma (GBT) examinations occur two days per week at the SMF during spill.  Please go to http://www.fpc.org/CurrentDaily/Gbtsum.txt for further details.

  - USDA - Avian hazing. Avian hazing continues.

  - University of Idaho. Cameras installed behind the Bradford Island picket leads to monitor lamprey and salmonid behavior. Lamprey trapping in conjunction with NOAA continues.

  - WDFW - Fish Counting.  Visual counting continues. Nighttime video lamprey counting continues.

- FISHWAYS

  - Project biologists inspected 08 through 14 July.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| SPILLWAY |  |  |  |  |
| 7/8-7/12, 14 | Bay 17 | Incorrect height | Hoist OOS | None |
| BRADFORD ISLAND (BI) |  |  |  |  |
| 7/8 | PH1 Chain gate 10B | Closed | Incorrect sensor | Ops adjusted in local |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |
| 7/8-13 | PH2CC entrances | Differential < 1.0’ | FU1 OOS | N/A |
| 7/8-13 | PH2CC entrances | Submergence < 13’ | FU1 OOS | N/A |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November. Temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 13 July.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - PH1 and B-branch SLEDs were removed on 28 June. Cascades Island and WA shore SLEDs are scheduled to be removed on 16 July.

    - All ladders remain in service.

      - All ladders were switched to Shad Mode on 04 June, congruous with FPP 2.5.1.2a. The Bradford Island and Cascades Island ladders were returned to Salmon Mode on 09 July and the WA Shore ladder was returned to Salmon mode on 10 July.

      - The WA Shore ladder was taken to 1 Fish Unit operations as outlined in table BON-13 in the FPP on 06 July after FU1 was forced out of service. The ladder was returned to normal operations on 13 July when FU1 returned to service.

    - The AFF remains in service.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC remains open.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPSs and associated traps remain in service.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 14 June states that, effective from 0001 hours on 16 June until 2400 hours on 31 August, operate in accordance with the 2012 Fish Operations Plan to provide spill for juvenile fish passage during the summer season at BON, as follows: 16 June – 21 July: Alternate between 2-day treatments of 95 kcfs 24 hours per day, and 85 kcfs day/121 kcfs night. 21 July – 31 August: 75 kcfs day/Gas cap night.

  - A teletype sent on 29 June requests that the BON pool be operated within a 1.5’ band, soft constraint, from 0600 hours 03 July to 1800 hours 06 July, and from 0600 hours 09 July to 1800 hours 11 July, during treaty fishing.

  - A teletype sent on 09 July updates the spill priority list order for Fish Passage Season for BON with associated total dissolved gas spill caps.

  - A teletype sent on 10 July requests that BON forebay be maintained between elevation 72.0-73.5’ as a hard constraint and 72.0-73.0 as a soft constraint from 1000 to 1500 hours each day, 16-20 July. This operation is needed for a kite boarding event at the port of Hood River.

  - A teletype sent on 10 July requests that BON forebay be maintained between 73.0-74.0’ as a soft constraint from 1000 until 1700 on 21 July, and a 73.5’ minimum pool as a soft constraint from 1000 until 1700 on 22 July.

JERRY CARROLL

Operations Project Manager