### CENWP-OD-B																						09 September 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 36 of 2012, which covers the period from 02 through 08 September 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 100.8 to 162.6 kcfs.  Daily average project tailwater ranged from 10.0’ to 14.1’ msl.  Daily average powerhouse forebay elevation ranged from 74.8’ to 75.4’ msl.  Daily average water temperature ranged from 68ºF to 69ºF. Secchi disk measurements ranged from 5.0 to 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours. Daily average spill ranged from 1.3 to 10.0 kcfs.

  - Unit Operation.  Powerhouse Two is the priority powerhouse until 16 September.

    - Unit 5 was out of service from 0819 to 0851 on 03 September for unit priority rotation.

    - Unit 11 was out of service from 0233 to 1856 on 02 September for governor trouble.

    - Unit 14 went out of service at 0710 on 11 June for a 4 year overhaul. It was returned to service at 1949 on 6 September and went out of service again at 1648 on 7 September for governor trouble.

    - Unit 15 went out of service at 0006 on 27 August for T12 bi-annual.

    - Unit 16 went out of service at 0006 on 27 August for T12 bi-annual.

    - Unit 17 went out of service at 0735 on 01 August for air gap monitor installation.

    - Unit 18 went out of service at 0006 on 27 August for T12 and annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed for cleaning from 1613 until 1622 on 08 September.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11,12,18 | N/A | N/A | STSs installed |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. The following dewatering or fish salvage activities occurred this week.

    - On 05 September, project biologists recovered 1 smallmouth bass and 25 sculpin from the Unit 14 tail logs. The fish were returned to the tailrace in good condition.

- RESEARCH

  - Battelle/PNNL – JMF Juvenile Assessment.  Juvenile growth study began the week of 27 August but due to temperature concerns, has been postponed until spring 2013. All previously collected fish were released.

  - Battelle/PNNL – Survival Study. Hydrophones remain installed.

  - CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF continues.

  - NOAA – Lamprey. LPS count network installed. Tagging at the CI LPS and the AFF concluded 07 September. Trap and haul from the CI LPS to the Stevenson release site continues.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Truck releases of summer out-migrants originating from McNary, Lower Granite, Little Goose, and Lower Monumental dams began on 18 August. Fallbacks were recorded crossing the separator bars this week: 1 unknown salmonid. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm.

  - University of Idaho. Lamprey trapping in conjunction with NOAA concluded on 01 September.

  - WDFW – AFF. Sampling for alternative gear study control group began the week of 27 August.

  - WDFW – Fish Counting.  Visual counting continues. Nighttime video lamprey counting continues.

  - WDFW – Tule Counting. Visual counting continues.

- FISHWAYS

  - Project biologists inspected 02 through 08 September.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location | FPP Items | Cause | Response |
| --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |
| 9/2-9/8 | A-branch | FG3-5 open w/<16.7 TW | Failed motor | TR in place |
| 9/2, 9/8 | B-branch | Ent. differential > 2.0 | FV 4-4 damaged | Repairs scheduled |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |
| 9/2, 9/8 | Weir 38 | Water level < 0.9’ | W37 bleed-off incorrect position | Ops adjusted |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties. The temperatures below are provided via this website and show the averages for BON forebay.

| Date | Temperature (F) |
| --- | --- |
| 9/2 | 67.5 |
| 9/3 | 67.3 |
| 9/4 | 67.4 |
| 9/5 | 67.7 |
| 9/6 | 67.8 |
| 9/7 | 67.8 |
| 9/8 | 67.8 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 07 September.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - All ladders remain in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate appears to be sheared from its attachment point on the wall. The ladder is currently being operated as close to FPP criteria as possible. Repairs are scheduled to start 01 October.

    - The AFF remains in service.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC remains open. It was closed from 0844 until 1500 on 4 September to facilitate an inspection of the concrete and possible repairs.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - All LPSs and associated traps remain in service except for the WA shore NDE trap.

    - On 16 August, NOAA personnel and Project Fisheries observed lamprey in the FV 5-9 AWS. A portable trap was installed in this area to trap lamprey and transport them, with the fish collected in the CI LPS, to the Stevenson release site.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. Construction continues. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 22 August requested that the river outflow at BON and TDA be maintained as low and as constant as possible from 0600 – 1200 hours on 03 September, with flows not to exceed 150 kcfs, for a cross-channel swim near Hood River, OR.

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the change of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that effective 0001 hours on September 1, the PH2 Corner Collector (B2CC) will be operated any time one or more unscreened units are operating at PH2, with the exception of September 4 (0700-1700), when it will be closed for repairs. The B2CC will be closed on September 16 through November 11 for repairs. Additionally, on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 31 August updates the spill priority list order for non-fish related spill season for BON with associated total dissolved gas spill caps.

  - A teletype sent on 09 September requests that the BON pool be operated within a 1.5’ band, hard constraint, for these periods: 0600 on 21 August to 1800 on 23 August, from 0600 on 27 August to 1800 on 30 August, from 0600 on 04 September to 1800 on 08 September and from 0600 on 11 September to 1800 on 14 September. The goal of this operation is to limit pool fluctuation for treaty fishing.

JERRY CARROLL

Operations Project Manager