### CENWP-OD-B																						30 September 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 39 of 2012, which covers the period from 23 through 29 September 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 94.6 to 114.3 kcfs.  Daily average project tailwater ranged from 9.3’ to 10.9’ msl.  Daily average powerhouse forebay elevation ranged from 74.1’ to 75.2’ msl.  Daily average water temperature ranged from 66ºF to 67ºF. Secchi disk measurements remained at 7.0’.

  - Spill Bays 1 and 18, which provide attraction flow for Cascades Island and B-branch, respectively, are open 6” during daylight hours. Daily average spill ranged from 0.6 to 1.2 kcfs.

    - Spillbay 1 was closed from 1156 until 1604 for a ROV inspection of the stilling basin.

    - Spillbay 18 was closed on 25 September for dewatering B-branch. It will remain closed until B-branch returns to service.

  - Unit Operation.  Powerhouse One is the priority powerhouse as of 16 September.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

    - Unit 15 went out of service at 0006 on 27 August for T12 bi-annual. The unit was returned to service at 1050 on 25 September.

    - Unit 16 went out of service at 0006 on 27 August for T12 bi-annual. The unit was returned to service at 1050 on 25 September.

    - Unit 17 went out of service at 0735 on 01 August for air gap monitor installation. The unit was returned to service at 0922 on 26 September.

    - Unit 18 went out of service at 0006 on 27 August for T12 and annual maintenance. The unit was returned to service at 1315 on 25 September.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed for cleaning from 1101 until 1130 on 25 September and from 1615 until 1625 on 28 September.

    - FV 3-9 was closed for dewatering B-branch at 1709 on 25 September.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11,12,18 | N/A | N/A | STSs installed |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. The following dewatering or fish salvage activities occurred this week.

    - On 25 September Project Biologists recovered between 75 and 100 White sturgeon from the Unit 11 draft tube. The fish were released into the forebay in good condition.

    - On 25 September Project Biologists recovered between 30 and 40 salmonids from the B-branch ladder. The fishes were released back into the ladder at the junction pool in good condition.

    - On 27 September Project Biologists recovered 1 adult Chinook and 1 Largescale sucker from the B-branch entrance bay. The fishes were released into the forebay in good condition.

- RESEARCH

  - Battelle/PNNL – Survival Study. Hydrophones remain installed.

  - CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF continues.

  - NOAA – Lamprey. LPS count network installed.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Truck releases of summer out-migrants originating from McNary, Lower Granite, Little Goose, and Lower Monumental dams began on 18 August. Fallbacks were recorded crossing the separator bars this week: 1 salmon. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm.

  - WDFW – AFF. Sampling for alternative gear study control group continues.

  - WDFW – Fish Counting.  Visual counting continues. Nighttime video lamprey counting continues.

  - WDFW – Tule Counting. Visual counting continues.

- FISHWAYS

  - Project biologists inspected 23 through 23 September.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location | FPP Items | Cause | Response |
| --- | --- | --- | --- | --- |
| 9/23 | Unit 18 | Run out of priority | 115 kV line restrictions | N/A |
| BRADFORD ISLAND (BI) |  |  |  |  |
| 9/25-29 | B-branch ladder | Out of service | Dewatered to repair FV 4-4 | N/A |
| CASCADES ISLAND (CI) – Nothing to report. |  |  |  |  |
| WASHINGTON SHORE (WS) |  |  |  |  |
| 9/23, 27, 29 | Weir 37 | Water level < 0.9’ | Unknown | None |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 28 September.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - All ladders remain in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance on 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF remains in service.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC closed on 16 September.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The Cascades Is. LPS was taken out of service on 20 September. Bradford Island and WA Shore LPSs remain in service.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. Construction continues. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

  - Spillbay 17. Final repairs to the hoist and the installation of new wire rope began on 17 September.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the change of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that effective 0001 hours on September 1, the PH2 Corner Collector (B2CC) will be operated any time one or more unscreened units are operating at PH2, with the exception of September 4 (0700-1700), when it will be closed for repairs. The B2CC will be closed on September 16 through November 11 for repairs. Additionally, on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 17 September updates the spill priority list order for non-fish related spill season for BON with associated total dissolved gas spill caps.

  - A teletype sent on 25 September requests that the BON pool be operated within a 1.5’ band, as a soft constraint from 0600 to 1800 on 18 September and as a soft constraint from 0600 on 26 September until 0600 on 27 September, and as a hard constraint from 0601 on 27 September until 1800 on 28 September in order to limit pool fluctuation for treaty fishing.

  - A teletype sent on 27 September states that effective immediately until further notice during daytime hours operate the BON forebay from 74.5 - 76.0’ as a hard constraint. This resets the treaty fishing zone. During nighttime hours operate the BON forebay from 73.5 – 76.0’ as a hard constraint. Operating above 75.5’ could over top the junction pool weir and flow into the dewatered B-branch. The goal of this operation is to facilitate repair work of the Bradford Island B-branch fish ladder and to minimize the duration A-branch ladder is outside of FPP criteria, while providing BPA with some flexibility for other concurrent operational constraints.

JERRY CARROLL

Operations Project Manager