### CENWP-OD-B																						07 October 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 40 of 2012, which covers the period from 30 September through 06 October 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 80.0 to 113.3 kcfs.  Daily average project tailwater ranged from 7.3’ to 10.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.9’ to 75.5’ msl.  Daily average water temperature ranged from 64ºF to 66ºF. Secchi disk measurements ranged from 5.5 to 7.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours. Spill bay 18 is closed for B-branch repairs. Daily average spill ranged from 0.6 to 0.7 kcfs.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 3 went out of service at 0909 on 01 October for a 5 year overhaul.

    - Unit 4 was out of service from 0850 until 1800 on 04 October for BPA line work.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

    - Unit 12 was out of service from 0951 until 1024 on 01 October for 2SU2 modifications.

    - Unit 13 was out of service from 1042 until 1141 on 01 October for 2SU2 modifications.

    - Unit 17 was out of service from 0006 on 01 October until 1612 on 04 October for bearing adjustment.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11,12,18 | N/A | N/A | STSs installed |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. The following dewatering or fish salvage activities occurred this week.

    - On 03 October Project Biologists recovered 17 White sturgeon from the Unit 3 draft tube. The fish were released into the tailrace in good condition.

- RESEARCH

  - Battelle/PNNL – Survival Study. Hydrophones remain installed.

  - CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF continues. Sampling will conclude before the end of the month.

  - NOAA – Lamprey. LPS count network installed.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Truck releases of summer out-migrants originating from McNary, Lower Granite, Little Goose, and Lower Monumental dams began on 18 August. Fallbacks were recorded crossing the separator bars this week: 1 salmon. Fallback observations are available at the FPC website: http://www.fpc.org/adultsalmon/bonkeltcounts.htm.

  - WDFW – AFF. Sampling for alternative gear study control group continues. Sampling will conclude before the end of the month.

  - WDFW – Fish Counting.  Visual counting continues. Nighttime video lamprey counting concluded on 30 September. Visual counting will conclude on 31 October.

  - WDFW – Tule Counting. Counting concluded on 30 September.

- FISHWAYS

  - Project biologists inspected 30 September through 06 October.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location | FPP Items | Cause | Response |
| --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |
| All week | BI weir | Water level < 0.9’ | B-branch dewatered | N/A |
| All week | A-branch | Water level > 1.1’ | B-branch dewatered | N/A |
| All week | B-branch ladder | Out of service | Dewatered to repair FV 4-4 | N/A |
| CASCADES ISLAND (CI) |  |  |  |  |
| 10/1 | FG 6-12-14 | Not closed for current TW | In manual | Ops adjusted |
| WASHINGTON SHORE (WS) |  |  |  |  |
| 10/2-3, 5-6 | Weir 37 | Water level not in criteria | In manual | Ops adjusted |
| 10/6 | Weir 38 | Water level not in criteria | W37 Bleed-off in manual | Ops adjusted |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 05 October.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - All ladders remain in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance during 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF remains in service.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC closed on 16 September.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2013.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The Cascades Is. LPS was taken out of service on 20 September. Bradford Island and WA Shore LPSs remain in service.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. Construction continues. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

  - Spillbay 17. Final repairs to the hoist and the installation of new wire rope continue.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the change of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that effective 0001 hours on September 1, the PH2 Corner Collector (B2CC) will be operated any time one or more unscreened units are operating at PH2, with the exception of September 4 (0700-1700), when it will be closed for repairs. The B2CC will be closed on September 16 through November 11 for repairs. Additionally, on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 17 September updates the spill priority list order for non-fish related spill season for BON with associated total dissolved gas spill caps.

  - A teletype sent on 27 September states that effective immediately until further notice during daytime hours operate the BON forebay from 74.5 - 76.0’ as a hard constraint. This resets the treaty fishing zone. During nighttime hours operate the BON forebay from 73.5 – 76.0’ as a hard constraint. Operating above 75.5’ could over top the junction pool weir and flow into the dewatered B-branch. The goal of this operation is to facilitate repair work of the Bradford Island B-branch fish ladder and to minimize the duration A-branch ladder is outside of FPP criteria, while providing BPA with some flexibility for other concurrent operational constraints.

  - A teletype sent on 01 October requests that the BON pool be operated within a 1.5’ band, as a soft constraint from 0600 on 02 October until 1800 on 03 October and as a hard constraint from 1801 on 03 October until 1800 on 04 October, in order to limit pool fluctuation for treaty fishing.

  - A teletype sent on 04 October requests that, effective from 0800 until 1400 on 05 October, no spillway release at BON beyond the fish attraction releases specified in the referenced CBT (BON R 083012 1235 Spillbay 17). A survey boat will be in the BRZ during these six hours.

JERRY CARROLL

Operations Project Manager