### CENWP-OD-B																						28 October 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2012, which covers the period from 21 through 27 October 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 95.0 to 136.5 kcfs.  Daily average project tailwater ranged from 9.3’ to 12.2’ msl.  Daily average powerhouse forebay elevation ranged from 75.1’ to 75.4’ msl.  Daily average water temperature ranged from 59ºF to 61ºF. Secchi disk measurements ranged from 6.0 to 7.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours. Spill bay 18 is closed for B-branch repairs. Daily average spill ranged from 0.6 to 1.1 kcfs.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 3 went out of service at 0909 on 01 October for a 5 year overhaul.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV1-1 was closed for cleaning from 1044 to 1052 on 23 October.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11,12,18 | N/A | N/A | STSs installed |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - Battelle/PNNL – Survival Study. Hydrophones remain installed.

  - CRITFC – AFF.  Annual Chinook, Coho, Sockeye and Steelhead sampling in the AFF concluded on 11 October.

  - NOAA – Lamprey. LPS count network installed.

  - PSMFC – Smolt Monitoring Program.  Juvenile fish condition and index monitoring continues. Truck releases of summer out-migrants originating from upriver sites will conclude on 31 October. No fallbacks were recorded crossing the separator bars this week. Fallback observations are available at the FPC website:  http://www.fpc.org/adultsalmon/bonkeltcounts.htm.

  - WDFW – AFF. Sampling for alternative gear study control group concluded on 11 October.

  - WDFW – Fish Counting.  Visual counting will conclude on 31 October.

- FISHWAYS

  - Project biologists inspected 21 through 27 October.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location |  | FPP Items | Cause |  |  | Response |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |  |
| All week | A-branch |  | FG3-3 half open | Mechanically bound |  |  | TR in place |
| All week | BI weir |  | Water level < 0.9’ | B-branch dewatered |  |  | N/A |
| All week | A-branch |  | Water level > 1.1’ | B-branch dewatered |  |  | N/A |
| All week | B-branch ladder |  | Out of service | Dewatered to repair FV 4-4 |  |  | N/A |
| CASCADES ISLAND (CI) – Nothing to report |  |  |  |  |  |  |  |
| 10/23 | FG3-12 | Not open for TW level |  |  | In manual | Ops adjusted |  |
| WASHINGTON SHORE (WS) – Nothing to report |  |  |  |  |  |  |  |
| 10/24,26 | Weir 37 | Water level < 0.8 |  |  | N/A | None |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 25 October.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - All ladders remain in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance during 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF remains in service.

  - Juvenile Fishways.

    - DSM2 remains in service.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The hydrocannon remains in service.

    - The B2CC closed on 16 September.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2012/13.

    - The spillway avian array was removed on 11 October to facilitate barge access for spillway erosion repair. The array will be reinstalled during the winter of 2012/13.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The Cascades Is. LPS was taken out of service on 20 September. Bradford Island and WA Shore LPSs remain in service.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the change of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that effective 0001 hours on September 1, the PH2 Corner Collector (B2CC) will be operated any time one or more unscreened units are operating at PH2, with the exception of September 4 (0700-1700), when it will be closed for repairs. The B2CC will be closed on September 16 through November 11 for repairs. Additionally, on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 17 September updates the spill priority list order for non-fish related spill season for BON with associated total dissolved gas spill caps.

  - A teletype sent on 27 September states that effective immediately until further notice during daytime hours operate the BON forebay from 74.5 - 76.0’ as a hard constraint. This resets the treaty fishing zone. During nighttime hours operate the BON forebay from 73.5 – 76.0’ as a hard constraint. Operating above 75.5’ could over top the junction pool weir and flow into the dewatered B-branch. The goal of this operation is to facilitate repair work of the Bradford Island B-branch fish ladder and to minimize the duration A-branch ladder is outside of FPP criteria, while providing BPA with some flexibility for other concurrent operational constraints.

  - A teletype sent on 25 October states that effective 25 October until further notice, BPA is requested to provide a minimum of one hour notice prior to spill, with a day-ahead notice preferred if possible due to ongoing spillway repair work and related safety concerns.

JERRY CARROLL

Operations Project Manager