### CENWP-OD-B																						18 November 2012

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 47 of 2012, which covers the period from 18 through 24 November 2012.

- OPERATION SUMMARY

  - Daily average river flows ranged from 138.6 to 146.5 kcfs.  Daily average project tailwater ranged from 13.2’ to 15.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.2’ to 74.3’ msl.  Daily average water temperature ranged from 51ºF to 54ºF. Secchi disk measurements ranged from 0.5 to 6.5’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours. Spill bay 18 is closed for B-branch repairs. Daily average spill remained at 1.1 kcfs.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

    - Unit 12 was out of service from 0700 to 1636 on 20 November for SQ2 work.

    - Unit 13 went out of service at 1100 on 16 November for oil leakage. It was returned to service at 1541 on 21 November.

    - Unit 14 was out of service from 0700 to 1636 on 20 November for SQ2 work.

    - Unit 15 was out of service from 0700 to 1636 on 20 November for SQ2 work.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 went out of service at 0000 on 10 November for winter maintenance.

    - F2 went out of service at 0000 on 10 November for winter maintenance.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  The following AWS closures occurred this reporting week.

    - FV 1-1 was closed for cleaning from 0658 to 0707 on 19 November.

    - FV 3-7 was closed for cleaning from 0807 to 0845 on 20 November.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | N/A | N/A | Unit 11 OOS |
| 12,18 | N/A | N/A | STSs installed, VBSs removed on 11/05 |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage.

    - On 20 November, 5 suckers and 1 small-mouth bass were removed from the south entrance pool of the PH2CC.

    - On 21 November, 12 sculpin were removed from Unit 13 tail logs.

- RESEARCH

  - Battelle/PNNL – Survival Study. Hydrophones remain installed.

  - NOAA – Lamprey. LPS count network installed.

  - WDFW – Fish Counting.  Visual counting concluded on 31 October.  Video counting began 01 November.

- FISHWAYS

  - Project biologists inspected 18 through 24 November. NOAA inspected on 23 November.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location | FPP Items | Cause | Response |
| --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |
| All week | A-branch | FG3-3 half open | Mechanically bound | TR in place |
| All week | BI weir | Water level < 0.9’ | B-branch dewatered | N/A |
| All week | A-branch | Water level > 1.1’ | B-branch dewatered | N/A |
| All week | B-branch ladder | Out of service | Dewatered to repair FV 4-4 | N/A |
| CASCADES ISLAND (CI) – Nothing to report |  |  |  |  |
| WASHINGTON SHORE (WS) – OOS |  |  |  |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 23 November.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - The WA Shore ladder was dewatered to tailwater on 13 November, and below tailwater on 15 November.

    - The south entrance pool of the PH2CC was dewatered on 20 November to allow access to the AWS for sand removal.

    - The Cascades Island fish ladder exit was opened on 08 November.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance during 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF was dewatered on 07 November.

  - Juvenile Fishways.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The JMF was dewatered and winterized on 05 November.

    - The hydrocannon was winterized on 05 November.

    - The DSM2 was dewatered on 11 November.

    - The B2CC closed on 16 September.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2012/13.

    - The spillway avian array was removed on 11 October to facilitate barge access for spillway erosion repair. The array will be reinstalled during the winter of 2012/13.

  - Lamprey Fishways.

    - The Cascades Is. entrance weir remains installed.

    - The Cascades Is. LPS was taken out of service on 20 September.

    - The WA shore LPS was taken out of service on 11 November.

    - The Bradford Island LPS remains in service.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

  - Spillway Erosion Repair. Rock removal and erosion cavity repair continues.

  - WA Shore LPS/LFS Installation. Installation of an entrance and flume has begun. The contractor will also repair expansion joints in the north monolith AWS.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the chance of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that effective 0001 hours on September 1, the PH2 Corner Collector (B2CC) will be operated any time one or more unscreened units are operating at PH2, with the exception of September 4 (0700-1700), when it will be closed for repairs. The B2CC will be closed on September 16 through November 11 for repairs. Additionally, on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 30 October states that effective immediately until further notice operate the BON forebay 24 hours a day from 71.5 - 76.0’ as a hard constraint. The goal of this operation is to facilitate repair work of the Bradford Island B-branch fish ladder and to minimize the duration A-branch ladder is outside of FPP criteria, while providing BPA with some flexibility for other concurrent operational constraints.

  - A teletype sent on 21 November updates the spill notification for the spillway stilling basin repair work. Effective immediately and until further notice, BPA is requested to provide a minimum of one hour notice prior to spill, with a day-ahead notice preferred if possible due to ongoing spillway repair work and related safety concerns. Due to ongoing B-branch repairs and chum operations, BON operators are requested to use NWP-provided spill tables and coordinate with construction oversight to safely evacuate workers and to notify BPA when it is safe to commence spill.

  - A teletype sent on 21 November updates the flow operations necessary to maintain a daytime tailwater appropriate for daytime chum spawning, effective until further notice. As a hard constraint, maintain the tailwater within a 0.6’ band of 12.2’ – 12.8’ during the daytime with a target elevation of 12.5’. To pass water the project is authorized to increase the tailwater elevation to 18.5’ during the nighttime between 1700-0600 hours, and if possible concentrate the highest tailwater elevations around midnight without exceeding 16.5’. If these operations are not sufficient to maintain the hard constraint, the daytime tailwater is authorized to increase to a maximum of 13.5’. The maximum hourly elevation reached during the daytime will become the new hard constraint target within the 0.6’ band.

JERRY CARROLL

Operations Project Manager