### CENWP-OD-B																						22 January 2013

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 03 of 2013, which covers the period from 13 January through 19 January 2013.

- OPERATION SUMMARY

  - Daily average river flows ranged from 169.0 to 206.2 kcfs.  Daily average project tailwater ranged from 14.8’ to 17.2’ msl.  Daily average powerhouse forebay elevation ranged from 72.3’ to 73.9’’ msl.  Daily average water temperatures ranged from 39ºF to 40ºF. Secchi disk measurements ranged from 6.0 to 7.0.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours. Spill bay 18 is closed as B-branch is out of service for repairs on FV 4-4. Daily average spill remained at 1.1 kcfs all week.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

    - Unit 16 was out of service from 0400 on 14 January to 0941 on 15 January for PH2 forebay dredging.

    - Unit 17 went out of service at 0400 on 14 January for PH2 forebay dredging.

    - Unit 18 went out of service at 0400 on 14 January for PH2 forebay dredging.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 went out of service at 0000 on 10 November for winter maintenance.

    - F2 went out of service at 0000 on 10 November for winter maintenance.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | N/A | N/A | Unit 11 OOS |
| 12,18 | N/A | N/A | STSs installed, VBSs removed on 11/05 |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - WDFW – Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 14 January through 17 January.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location |  | FPP Items | Cause |  | Response |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |
| 01/14 | WG-2 |  | Gate Submergence | N/A |  | TR in place |
| 01/15-16 | WG-64 |  | Gate Submergence | N/A |  | TR in place |
| All week | B-branch ladder |  | Out of service | Dewatered to repair FV4-4 |  | N/A |
| 01/15-17 | PH1CC |  | South diff < 1.0’ | B-branch dewatered |  | N/A |
| All week | A-branch |  | FG3-3 half open | Mechanically bound |  | TR in place |
| All week | A-branch |  | Water level > 1.1’ | B-branch dewatered |  | N/A |
| All week | BI weir |  | Water level < 0.9’ | B-branch dewatered |  | N/A |
| 01/15 | FV1-1 |  | Differential >0.5’ | Debris accumulation |  | Cleaned |
| CASCADES ISLAND (CI) |  |  |  |  |  |  |
| 01/09 |  | CI Fishway | Differential <1’ | Diffusers in manual | Ops adjusted |  |
| 01/17 |  | FG6-10 | Not open correctly for given TW | Diffusers in manual | Ops adjusted |  |
| WASHINGTON SHORE (WS) – OOS |  |  |  |  |  |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November. BON site specific temperatures are unavailable this week due to technical difficulties.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibrations were checked on 14 January and 17 January.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDs are removed from all entrances.

    - The WA Shore ladder and North and South Monoliths at PH2 remain dewatered.

    - The Cascades Island fish ladder exit remains in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance during 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF remains dewatered.

  - Juvenile Fishways.

    - The PH1 ice and trash sluiceway (ITS) remains in service. Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The JMF remains dewatered and the hydrocannon winterized.

    - The DSM2 remains dewatered.

    - The B2CC remains dewatered.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2012/13.

    - The spillway avian array was removed on 11 October to facilitate barge access for spillway erosion repair. The array will be reinstalled during the winter of 2012/13.

  - Lamprey Fishways.

    - All LPSs remain dewatered.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

  - Spillway Erosion Repair. Rock removal and erosion cavity repair continues.

  - WA Shore LPS/LFS Installation. Construction continues.

  - Fish Unit Dredge. Dredging to remove sediment from the fish unit intake area commenced on 14 January, 2013.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the chance of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 21 November updates the spill notification for the spillway stilling basin repair work. Effective immediately and until further notice, BPA is requested to provide a minimum of one hour notice prior to spill, with a day-ahead notice preferred if possible due to ongoing spillway repair work and related safety concerns.

  - A teletype sent on 11 December requests that tailwater be maintained at a maximum of 21.0’ from 1500 hours on 10 December 2012 until 1800 hours on 25 January 2013. If high flows preclude maintaining tailwater at a 21.0’ maximum, BPA is requested to provide as much notification as possible to the BON control room.  Notification hours are provided.  If a tailwater above 21.0’ is pending, BON control room is requested to notify construction oversight for evacuation of the lamprey caisson area or Fowler Construction directly.

  - A teletype sent 13 December updates the winter spill priority list and wintertime spill caps.

  - A teletype sent on 20 December updates the flow operations necessary to maintain a daytime tailwater appropriate for daytime chum spawning and to pass excess water, effective until further notice.  As hard constraint #1, maintain the tailwater at a minimum of 13.5’ at all hours.  As a hard constraint #2, maintain tailwater during the daytime within a 2.0’ band of 13.5’ – 15.5’ with a target of 14.0’.

  - A teletype send on 03 January states that effective immediately until further notice operate the BON forebay 24 hours a day from 71.5’ – 76.5’ as a hard constraint. This cancels the maximum forebay elevation of 76.0’ in a previous teletype, which is not currently needed. In the future additional maintenance will be required at which time the project will request reverting back to a hard constraint of 76.0’ for personnel access to the B-branch ladder.

  - A teletype sent on 11 January requests that due to the high priority of the spillway repair work, if high flows or any other circumstance requires the operation of PH1 units 16-18, that BPA provide at minimum one hour notice to the BON operator, with as many hours of notification as possible.  This is to allow initiation of evacuation of the PH1 forebay dredge. An outage of PH1 Units 16-18 is currently scheduled from 0400 14 January through 1700 on 31 January for the dredge work. BON will work with the dredge contractor to see if Unit 16 can return to service during some or all hours.

  - A teletype sent on 18 January requests that effective immediately until 1800 on 26 January, the forebay minimum elevation be 72.5 ft as a hard constraint and above 73.0 ft as a soft constraint.  This request is to avoid grounding of the fish unit dredging operations at PH2.

JERRY CARROLL

Operations Project Manager