### CENWP-OD-B																						04 February 2013

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 05 of 2013, which covers the period from 27 January through 02 February 2013.

- OPERATION SUMMARY

  - Daily average river flows ranged from 140.1 to 174.3 kcfs.  Daily average project tailwater ranged from 13.7’ to 15.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 74.8’ msl.  Daily average water temperatures ranged from 37ºF to 38ºF. Secchi disk measurements ranged from 6.5’ to 7.0’.

  - Spill Bays 1 and 18 provide attraction flow for Cascades Island and B-branch, respectively. Spill bay 1 is open 6” during daylight hours. Spill bay 18 is closed as B-branch is out of service for repairs on FV 4-4. Daily average spill remained at 1.1 kcfs all week.

  - Unit Operation.  Powerhouse One is the priority powerhouse.

    - Unit 06 went out of service from 0001 on 28 January to 1453 on 31 January for annual maintenance.

    - Unit 11 went out of service at 0800 on 25 September for high thrust bearing temperatures.

    - Unit 12 went out of service from 1247 to 1449 on 02 February for flow testing.

    - Unit 14 went out of service from 0700 to 1639 on 02 February for flow testing.

    - Unit 15 went out of service from 0905 to 1639 on 02 February for flow testing.

    - Unit 16 went out of service from 0700 to 0902 on 02 February for flow testing.

    - Unit 17 went out of service from 0400 on 14 January to 1931 on 30 January for PH2 forebay dredging and from 0855 to 1639 on 02 February for flow testing.

    - Unit 18 went out of service from 0400 on 14 January to 1931 on 30 January for PH2 forebay dredging and from 0700 to 1639 on 02 February for flow testing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore (WS) fish ladder.  The units may be placed on standby, as necessary, during nighttime hours to float debris.

    - F1 went out of service at 0000 on 10 November for winter maintenance.

    - F2 went out of service at 0000 on 10 November for winter maintenance.

  - Gatewell drawdowns are measured on Tuesdays and more frequently as needed.

- ACTIVITIES

  - Auxiliary Water System Closures.  No AWS closures occurred this reporting week.

  - STS/VBS inspections.  No STS/VBS inspection occurred this reporting week.

    - Table 1.  STS and VBS inspection.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | N/A | N/A | Unit 11 OOS |
| 12,18 | N/A | N/A | STSs installed, VBSs removed on 11/05 |
| 13-17 | N/A | N/A | STSs removed |

  - Dewatering and Fish Salvage. No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - WDFW – Fish Counting.  Video counting continues.

- FISHWAYS

  - Project biologists inspected 28 January through 31 January.

  - Fish Passage Plan Observations.

    - Table 2.  FPP Out of Criteria items.

| Date | Location |  | FPP Items | Cause |  | Response |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND (BI) |  |  |  |  |  |  |
| All week | WG-2 |  | Gate Submergence | N/A |  | TR in place |
| 01/30 | WG-64 |  | Gate Submergence | N/A |  | TR in place |
| All week | B-branch ladder |  | Out of service | Dewatered to repair FV4-4 |  | N/A |
| All week | PH1CC |  | South diff < 1.0’ | B-branch dewatered |  | N/A |
| 01/28-30 | PH1CC |  | North diff >2.0’ | B-branch dewatered |  | N/A |
| All week | A-branch |  | FG3-3 half open | Mechanically bound |  | TR in place |
| All week | A-branch |  | Water level > 1.1’ | B-branch dewatered |  | N/A |
| All week | BI weir |  | Water level < 0.9’ | B-branch dewatered |  | N/A |
| All week | FG3-5 |  | Not open correctly for given TW | Burnt-out motor |  | TR in place |
| CASCADES ISLAND (CI) |  |  |  |  |  |  |
| 01/29 |  | FG6-11 | Not open correctly for given TW | Diffusers in manual | Ops adjusted |  |
| 01/31 |  | FG6-19 | Not open correctly for given TW | Diffusers in manual | Ops adjusted |  |
| WASHINGTON SHORE (WS) – OOS |  |  |  |  |  |  |

    - PH1CC diffuser FG2-19 is partially open.  Repairs will occur when the PH1CC is dewatered. The next possible time period will be 2013/14 winter maintenance.

    - A new mechanical velocity meter has been fabricated for PH2 and is scheduled for installation.

  - Fishway Temperatures. Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 31 January.

    - 10 of 12 floating orifice gates (FOGs) are installed. Two gates remain out for maintenance.

    - SLEDS were installed for the north and south entrances of the PH1CC at 0930 on 31 January.  SLEDs are removed from all other entrances.

    - The WA Shore ladder and North and South Monoliths at PH2 remain dewatered.

    - The Cascades Island fish ladder exit remains in service.

    - On 09 August, FV 4-4 was discovered to be broken in the full open position. Upon ROV inspection, the gate was found to be sheared from its attachment point on the wall. B-branch was dewatered from the junction pool down to the entrance during 25-27 September to facilitate repairs on FV 4-4. A-branch and the upper Bradford Island ladder remain in service and are currently being operated as close to FPP criteria as possible.

    - The AFF remains dewatered.

  - Juvenile Fishways.

    - Manual chaingates 1A and 1B remain open and are both set to 70’ msl. Automated chaingates 3B, 6C and 10B are open and functioning in auto.

    - The JMF remains dewatered and the hydrocannon winterized.

    - The DSM2 remains dewatered.

    - The B2CC remains dewatered.

    - The B2CC avian array was removed to facilitate barge access for B-branch emergency repairs. The array will be reinstalled during winter of 2012/13.

    - The spillway avian array was removed on 11 October to facilitate barge access for spillway erosion repair. The array will be reinstalled during the winter of 2012/13.

  - Lamprey Fishways.

    - All LPSs remain dewatered.

- CONSTRUCTION

  - Seawater Recirculation System Removal (JMF). Removal continues.

  - Cascades Island LPS Continuation. This expansion will remove the evaluation trap box and continue the LPS flume to a volitional exit near the CI fishway exit.

  - Gantry 7 Rehabilitation. The Powerhouse 2 intake gantry crane went out of service on 01 August for rehabilitation. It is scheduled to return to service in February 2013.

  - Spillway Erosion Repair. Rock removal and erosion cavity repair continues.

  - WA Shore LPS/LFS Installation. Construction continues.

  - Fish Unit Dredge. Dredging to remove sediment from the fish unit intake area commenced on 14 January and continued throughout the week.

- HAZMAT, SPILLS AND CLEANUP. Nothing to report.

- TELETYPES CURRENTLY IN EFFECT

  - A teletype sent on 23 August updates the operation of BON project PH2 unscreened units (Units 13-17) to pass flow. This operation is necessary due to the rehabilitation of Gantry 7. During the Gantry 7 outage, the project will not be able to remove or install screens. Additionally, limit flow through PH2 screened units (Units 11, 12, and 18) to a maximum of 15 kcfs per unit. The intent of this limitation is to minimize the chance of damaging an operating screen during the Gantry 7 outage, which would force the unit out of service until February 2013.

  - A teletype sent on 23 August states that on 16 September PH1 will become the priority powerhouse.  In November, MU18 will be taken out of service and the VBS will be removed from MU11 and MU12, when the downstream migrant channel (DSM2) is dewatered for installation of a lamprey passage system. At that time, those units will be operated last in the priority order.

  - A teletype sent on 21 November updates the spill notification for the spillway stilling basin repair work. Effective immediately and until further notice, BPA is requested to provide a minimum of one hour notice prior to spill, with a day-ahead notice preferred if possible due to ongoing spillway repair work and related safety concerns.

  - A teletype sent 13 December updates the winter spill priority list and wintertime spill caps.

  - A teletype sent on 20 December updates the flow operations necessary to maintain a daytime tailwater appropriate for daytime chum spawning and to pass excess water, effective until further notice.  As hard constraint #1, maintain the tailwater at a minimum of 13.5’ at all hours.  As a hard constraint #2, maintain tailwater during the daytime within a 2.0’ band of 13.5’ – 15.5’ with a target of 14.0’.

  - A teletype sent on 03 January states that effective immediately until further notice operate the BON forebay 24 hours a day from 71.5’ – 76.5’ as a hard constraint. This cancels the maximum forebay elevation of 76.0’ in a previous teletype, which is not currently needed. In the future additional maintenance will be required at which time the project will request reverting back to a hard constraint of 76.0’ for personnel access to the B-branch ladder.

  - A teletype sent on 28 January requests that effective immediately and until 1800 February 1, the BON forebay minimum elevation be 72.5’ as a hard constraint and above 73.0’ as a soft constraint to avoid grounding of the dredging spoils barge on Cascade Island as it offloads.

  - A teletype sent on 29 January supersedes the previous teletype regarding the forebay restriction for valve repair work at the Bradford Island B-branch fish ladder.  Effective 0600 on 1 February through 1800 4 February, operate the BON forebay 24 hours per day from 71.5’ – 76.0’ as a hard constraint. At the expiration of this teletype, revert to the normal pool operating range of 71.5’ – 76.5’.

  - A teletype sent 31 January cancels the forebay restrictions and request for notification for dredge evacuation related to the dredge operations in the PH2 forebay.  Dredging operations are complete and the contractor has demobilized all equipment as of 0800 on 31 January.

  - A teletype send 31 January states that between 0800 on 2 February and 0600 on 3 February, all personnel and equipment are to be moved out of the BON spillway stilling basin and all spill bay clearances lifted.  The corner collector is to be off while the barge and tub are transiting.  When clearance lifting begins, the notification request prior to spill is suspended until the bays are again tagged out. Additionally, from 0600 to 2000 on 3 February, request spill of up to 50 kcfs as necessary to meet all non-emergency flow requirements at the project. If spill over 50 kcfs is required during the dive, open the corner collector. If additional flow is needed, BPA is requested to provide at least one-hour notification to remove divers and lift clearances. If clearances cannot be lifted fast enough to maintain the minimum tailwater of 13.5’, tailwater guidance is given. Starting at 0600 on 2 February, the locking of tagging out of all PH2 units is to commence for divers to remove the caisson at the north fish ladder. Once the dive is complete, the operator will coordinate with BPA to shift flow to PH2.

  - A teletype sent on 1 February states that between 1300 and 1500 hours on 3 February operate PH1 and PH2 to maintain tailwater elevation as close to 13.5’ as possible for a tailrace survey immediately downstream of PH2. During the survey it is requested that the flows at PH1 are maximized and at PH2 are minimized as much as possible to ensure safe conditions for the survey crew.

  - A teletype sent 1 February states that from 0600 on 4 February to 1600 on 6 February, all personnel and equipment are to be moved out of the BON spillway stilling basin. From 0600 to 1600 on 7 February and every day thereafter until further notice, all personnel and equipment are to be moved out of the stilling basin for spilling operations. The corner collector is to be off while the barge and tug are transiting and may remain off unless requested. Starting at 0600 on 4 February and at 0600 every day thereafter until further notice, all spillway clearances are to be lifted and flow shifted to the spillway. Once all units are tagged and locked OOS, divers and crew will work at the north fish ladder. On 4 and 5 February divers are to clear the PH2 area in time to allow PH2 clearances to be lifted and flow switched to PH2, and spillway clearances hung no later than 2000. The operator is to coordinate with BPA to shift flow from the spillway to PH2. On 6 February and every day thereafter until further notice, divers are to clear the PH2 area in time to allow PH2 clearances to be lifted and flow switched to PH2 and spillway clearances hung no later than 1600.  The operator is to coordinate with BPA to shift flow from the spillway to PH2. From 0600 to 2000 on 4 and 5 February, request spill of up to 60 kcfs as necessary to meet all non-emergency flow requirements. From 0600 to 1600 on 6 February and everyday thereafter until further notice, again request spill of up to 60 kcfs. If more spill is required, or if clearances on generating units cannot be lifted fast enough, additional operating guidance is outlined.

JERRY CARROLL

Operations Project Manager