### CENWP-OP-B                                                                                                      3 January 2000

MEMORANDUM FOR CENWP-OP, ATTN:  Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 52 of 1999, which covers the period 26 December through 1 January.

- OPERATION SUMMARY.

1.1. Daily average river flow ranged from 165.6 to 222.5 kcfs.  Daily average tailwater elevation for the project ranged from 15.1’ to 18.0’ msl.  River temperature ranged from 44 to 46° F.  Spill bay 1, which supplies attraction flow for the Cascades Island ladder remained on sill as of 8 December.  Spill bay 18, which supplies attraction flow for the B-branch ladder, remained open 4”.

- Unit 10 remained out of service for stator rewind.

- The first powerhouse ice and trash sluiceway remained open for debris removal and the second powerhouse sluiceway remained closed this reporting week.

- Second powerhouse fish units remained out of service for winter maintenance.

- ACTIVITIES.

2.1. AWS Closures.  FV1-1 was closed for cleaning from 1330-1400 on 29 December.  FV3-9 was closed for cleaning from 1500-1507 on 29 December.

2.2. Dewaterings and Fish Salvage.  There was no fish salvage this reporting week.

- RESEARCH.

3.1. Normandeau MGR Testing.  Normandeau and Mid-Columbia Consultants will resume biological MGR testing at units 5 and 6 on 5 January.

3.2. WDFW Fish Counting.  WDFW continued 24-h/d video counting at Bradford Island.

4.  FISHWAYS.  Project biologists inspected on 28, 29 and 30 December this reporting week.

4.1. Fish Passage Plan Observations.

| DATE | LOCATion | FPP VIOLATION | CAUSE | RESPONSE |
| --- | --- | --- | --- | --- |
| All Week | A-branch diffuser FG3-4. | Diffuser should be open at 14.4’ tailwater elevation and is stuck closed due to mechanical failure. | Diffuser gate is separated from its shaft and will not be repaired until the winter maintenance season. | Collection channel is maintaining criteria despite diffuser being out of service. |
| All Week | A-branch diffuser FG3-5. | Diffuser should be open at 17.4’ tailwater elevation and is stuck closed due to mechanical failure. | Diffuser gate is separated from its shaft and will not be repaired until the winter maintenance season. | Collection channel is maintaining criteria despite diffuser being out of service. |
| All Week. | PH1 collection channel electronic velocity meter. | Meter registered <1.5 fps and should register 1.5-4.0 fps. |  | No action taken. |

4.2. Sensor Calibration.  Water level sensors were checked for calibration on 30 December.

4.3. Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- CONSTRUCTION UPDATE.

  - Construction continues on the new Juvenile Monitoring Facility.

6.  OTHER NOTABLE ITEMS.

6.1. Fishway inspection dives are scheduled for 5 and 6 January.

6.2. The Washington shore ladder is scheduled to return to service on 10 January.

6.3. The Cascades Island ladder is schedule to return to service on 10 January.

6.4. The Bradford Island ladder is scheduled to be dewatered on 11 January.

DEBORAH L. CHENOWETH

# Operations Project Manager