## SR
FISHWAY STATUS REPORT | [6 empty] | JOHN DAY DAM
Date: | 2012-02-06 | [7 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 01/29 through 02/05/2012 | [6 empty] | P.O. Box 564
Rufus, OR 97050
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 1 | Temperature: |  | 37.1667 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 6 | Ft.
NORTH FISHWAY |  |  |  |  | OOS - dewatered since 7 November. ETR mid March 2012.
Exit differential |  |  |  | ≤ 0.5'
Exit Control weirs |  |  |  | Per forebay
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Entrance differential |  |  |  | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir EW1 |  |  |  | depth (≥ 8') | AVG | #DIV/0!
Entrance weir EW2 |  |  |  | No criteria
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5' | OOS- AWS pumps off on 1/29 PM, dewatered on 1/31. ETR on 2/13.
Exit Control weirs |  |  | 0 | Per forebay | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.3
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.3
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.7
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.2
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 8.9
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 8.9
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.6
Submersible traveling screens |  |  | 0 | visual inspect | All STSs removed for the winter maintenance by 1/3/2012. |  |  |  |  | ETR before 1 April.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | No discrepancies.
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly | No discrepancies
Spill volume |  |  | None | per FPP
Spill pattern |  |  | N/A | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: OOS for winter maintenance. ETR 31 March 2012
Maintenance: All flushing water pipes/valves were dewatered and SMF fully winterized by 11/18.
JBS collection channel is scheduled for its annual dewatering/ inspection on 7 February.
Research: None
OTHER ISSUES:
Birds: see bird tab.
JD tailrace BRZ Avian Lines repair and improvements' contract is ongoing. All 125 lines will be available/properly tensioned for the 2012 juvenile passage
season starting on 1 April. JD Engineering and Fisheries are involved in coordination as needed.
Operations:
JD North fishway continues dewatered/OOS since 11/7. ETR is mid March 2012.
JD South fishway's AWS pumps were off 1/29 PM, upper ladder dewatered on 1/31/2012. Total # of fish requiring salvage was small : 10 a lamprey,
2 a unclipped steelhead, and 13 juvenile salmonids. All fish were bagged and released into the river quickly and in excellent condition. Even smaller #
of fish including one a steelhead and one juvenile salmonid, were pushed downstream into the tailwater (inside of fishway.) ETR for JD South is 2/13.
New construction:
JD North entrance improvements, 2-years' contract by Slayden Group is underway. The first year's construction activities are to be completed by mid
March 2012.
JD South AWS turbine 3 rehab continues slightly behind schedule. ETR in early March, 2012. JD Maintenance is providing the contractor's support.
Maintenance:
All STS were removed for winter maintenance by 3 January 2012. ETR 1 April 2012.
JD South Fishway Automation is in service and working properly.
Gatewell drawdown: Conducted. All VBSs OK. All MU trashracks are raked as soon as their differential reaches 1.3' or higher.
Calibration: | 1/28/2012 All PLCs were accurate with a reading error of less than 0.3 '.
Research:
PNNL crew re-installed their powerhouse and spillway hydrophones (into deployment pipes at all forebay pier noses) during the week of 30 January.
No project support was required, except for JD Fisheries coordination of spillway safety clearance on 2/1 and 2/2.
JD Fisheries team continues planning/ coordination of the 2012 research activities scheduled to take place at JD during this upcoming season.

## FishCounts
Fish counts ended Oct. 31, 2011. To resume in the spring 2012.

## Birds
S2:no birds observed
S1: no birds observed
S3: No birds observed
P4: 6 cormorants
P3: 7 cormorants
P2: no birds observed
P1: no birds observed
S4: No birds observed

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 38 |  | 6 |  | 0
Mon | 38 |  | 6 |  | 0
Tues | 36 |  | 6 |  | 0
Wed | 37 |  | 6 |  | 0
Thur | 37 |  | 6 |  | 0
Fri | 37 |  | 6 |  | 0
Sat |  |  |  |  | 0
AVG: | 37.1667 | AVG: | 6 | AVG | 0
|  |  |  | MAX | 0
|  |  |  | MIN | 0
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 8.9 | 8.9 | 1.3 | 8.3 |  |  | 4.6 | 1.7 | 1.2
Sun
Mon
Mon
Tues
Tues
Wed
Wed
Thur
Thur
Fri
Fri
Sat
Sat
AVG: | 8.9 | 8.9 | 1.3 | 8.3 | #DIV/0! | #DIV/0! | 4.6 | 1.7 | 1.2