## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: | 2011-02-14 | [8 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 2/6/11 - 2/12/11 | [7 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 39 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 3.2857 | Ft.
NORTH FISHWAY |  |  |  |  | Returned back to service on 1/31/11. Meeting all FPP criteria since 2/1/11.
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for HIGH forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 1 | 1.0' - 2.0' | AVG | 1.7143 | Minor calibration issue - TR'd
Entrance weir EW1 |  |  | 0 | depth (≥ 8') | OOS
Entrance weir EW2 |  |  | 0 | depth (≥ 8') | AVG | 9.4
SOUTH FISHWAY |  |  |  |  | Orifice flow only on 2/1/11. Upper dewatered on 2/3/11. ETR is 2/28/11.
Exit differential |  |  | N/A | ≤ 0.5'
Exit Control weirs |  |  | N/A | Per forebay | Set for MID forebay
Count station differential |  |  | N/A | ≤ 0.3'
Weir crest depth |  |  | N/A | 1.0' ± 0.1'
South entrance differential |  |  | N/A | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir SE1 |  |  | N/A | depth (≥ 8') | AVG | #DIV/0!
Collection channel velocity |  |  | N/A | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | N/A | 1.0' - 2.0' | AVG | #DIV/0!
N.entrance PH(Bay 19)differential |  |  | N/A | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir NE1 |  |  | N/A | depth (≥ 8') | AVG | #DIV/0!
Entrance weir NE2 |  |  | N/A | depth (≥ 8') | AVG | #DIV/0!
JUVENILE PASSAGE |  |  |  |  | JBS collection channel and outfall were dewatered on 2/10.
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | visual inspect | All STSs were removed on 12/16 through 12/19/10. They will be reinstalled before 1 April
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly
Spill volume |  |  | 0 | per FPP | On Seal
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | OOS until 2001 passage season, starting on 1 April.
JBS collection channel and outfall conduit were dewatered on 2/10. 6 adult steelhead were bagged and returned back into the river in excellent condition.
Maintenance:
3 and 2 way gates have been already fixed; NOAA engineers recommended the "slack" running belts for their improved performance.
2010 extended operation resulted in the SMF flushing water pipes and valves being frozen/ cracked. All damages will be repaired before 1 April.
FPOM decided that it is critical to run SMF through November, but we have their permission to shut it down based on a freezing weather forecast.
PSMFC electrical crew completed updates to the SMF control system, they will allow access to various sampling settings in real time over the internet
PMs and repair activities are ongoing:
Screen cleaner repairs and maintenance underway.
PDS dewatering screens and their perf plates are being removed from guides and pressure washed by JD Structural.
New protective netting was installed by JD Structural to keep bird predators out and keep fish inside of the Emergency Overflow Channel (an occasional
adult salmon had been observed to jump into the dry drainage tank, once every few years.)
OTHER ISSUES:
JOHN DAY
Birds: | see bird tab
Contract with USDA Animal Control Unit is being processed for 2011 gull hazing coverage at JD tailrace to minimize predation on juvenile salmonids.
New construction: 15 kV tap's installation by contractor (for the North Ladder's future AWS pumps ) is almost complete.
JD Fisheries participating in JDN entrance improvements' design, surveys and inspections. Construction activities are planned of the next year.
BPA approved additional funding for completion of the JD South AWS turbine 3 rehab. Specific plans for this challenging job are formulated by the
Portland District's engineering team in coordination with JD Maintenance. ETR is March 2012.
Maintenance:
JD North fishway returned back to service on 31 January. There were few minor calibration/setting issues with its entrance weirs PLC and AWS pumps,
which were fixed by 2/1.
One out of six North AWS pumps is OOS due to the gear box failure. It won’t be repaired/ available during 2011 passage season; all six pumps
are scheduled for replacement the next year.
JD South fishway was dewatered to tail water on 2/3. 5 juvenile salmonids were bagged and released back into the river in excellent condition.
A few more fish were pushed with dip nets into tail water. Thanks to Tammy, Chris and Madeline from Portland District for their help!
JD South collection channel and SE-1 diffuser pool were dewatered on 2/8 and 2/9, 3 and 6 adult steelhead respectively were bagged and released
back into the river in excellent condition.
South Fishway's automation work will be completed in February as the appropriate funding is being dropped soon.
Calibration: Conducted on 2/07, all were within established limits.
Operations:
Only one adult fishway, JD North is in regular service and meeting all FPP criteria since 2/1 (JD South OOS since 2/1.)
Good news ! North Ladder's CS crowder box window and auto cleaning brush repairs are completed.
After prolonged outage in 2010, the JD trashrack gentry has been repaired. It is now available for service.
STS camera device 's old video system failed beyond repair at the end of August '10 inspection. JDE(Electrical) is replacing it with brand new
cameras / hardware during this winter outage. RTS is April 2011.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Research:
U of I radiotelemetry crew performed maintenance of their JD South antenna grid on 2/9- 2/10. JD Structural provided crane and man basket support.
Regional lamprey task group inspected the JDS fishway and identified a number of potential passage improvements on 2/10.
Planning for 2011 research activities is underway.
U of I continues with adult lamprey PIT detections and with adult salmonids radiotelemetry tracking at both JD ladders.
Approved by Jerry Carroll
Operation Project Manager
John Day Dam

## Birds
S2:
S1: No birds observed
S3:
P4:
P3:
P2:
P1: NO birds observed
S4:

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 39 |  | 3
Mon | 39 |  | 3
Tues | 39 |  | 3
Wed | 39 |  | 3.5
Thur | 39 |  | 2.5
Fri | 39 |  | 3.5
Sat | 39 |  | 4.5
AVG: | 39 | AVG: | 3.2857 | AVG | #DIV/0!
|  |  |  | MAX | 0
|  |  |  | MIN | 0
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun |  |  |  |  | 2.3 | 9
Sun
Mon |  |  |  |  | 1.7 | 9 | 1.43
Mon
Tues |  |  |  |  | 1.5 | 9.4 | 1.32
Tues
Wed |  |  |  |  | 1.5 | 9 | 1.33
Wed
Thur |  |  |  |  | 1.7 | 10.7
Thur
Fri |  |  |  |  | 1.8 | 10.5
Fri
Sat |  |  |  |  | 1.5 | 8
Sat
AVG: | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.7143 | 9.3714 | 1.36 | #DIV/0! | #DIV/0!