## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: |  | 2012-03-03 | [7 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 2/26 to 3/3/2012 | [7 empty] | P.O. Box 564
Rufus, Oregon 97050
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 10 | Temperature: |  | 40.5714 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 5.5714 | Ft.
NORTH FISHWAY |  |  |  |  | OOS - dewatered since 7 November. ETR mid March 2012.
Exit differential |  |  |  | ≤ 0.5'
Exit Control weirs |  |  |  | Per forebay | Set for HIGH forebay
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Entrance differential |  |  |  | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir EW1 |  |  |  | depth (≥ 8') | AVG | #DIV/0!
Entrance weir EW2 |  |  |  | No criteria | Weir closed
SOUTH FISHWAY |  |  |  |  | Returned to service on schedule, 2/13 late PM, with two AWS turbines.
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.28
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.59
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.53
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.2
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 8.91
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 8.87
JUVENILE PASSAGE |  |  |  |  | JBS collection channel is OOS for maintenance since 02/07/2012
Forebay/bypass conduit differential |  |  |  | 4.0' - 5.0' | AVG | #DIV/0!
Submersible traveling screens |  |  |  | visual inspect | All STSs removed for the winter maintenance by 1/3/2012. | [5 empty] | ETR before 1 April.
Turbine trashrack drawdown |  |  |  | <1.5', wkly | No discrepancies.
Vert barrier screen drawdown |  |  |  | <1.5', wkly | No discrepancies
Spill volume |  |  |  | per FPP
Spill pattern |  |  |  | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: OOS for winter maintenance. ETR 31 March 2012
Maintenance: JBS collection channel was dewatered for its annual dewatering/ inspection on 7 February; the tainter gate crack's investigation ongoing.
Research: Coordinating with the fisheries contractors for 2012 passage season.
Fallbacks | AVG | 0 | MAX | 0 |  | MIN | 0
OTHER ISSUES:
JOHN DAY
Birds: | see bird tab
Calibration: | 3/3/12 All in criteria
Research:

## FishCounts
John Day 2011
| South | North | South | North | South | North | South | North | South | North
| ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd | Sockeye | Sockeye | Lamprey | Lamprey

## Birds
S2: No bird
observed
S1: No birds observed
S3: 7 Cormorant
P4: 1 Cormorant
P3: 1 Gull 8 Cormorant
P2: No bird
observed
P1: NO birds observed
S4 No bird observed

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 40 |  | 5 |  | 0
Mon | 41 |  | 5 |  | 0
Tues | 41 |  | 6 |  | 0
Wed | 40 |  | 6 |  | 0
Thur | 40 |  | 6 |  | 0
Fri | 41 |  | 6 |  | 0
Sat | 41 |  | 5 |  | 0
AVG: | 40.5714 | AVG: | 5.5714 | AVG | 0
|  |  |  | MAX | 0
|  |  |  | MIN | 0
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 9 | 8.9 | 1.3 | 8.4 |  |  |  | 1.8 | 1.4
Sun
Mon | 9.1 | 9.1 | 1.1 | 8.7 |  |  |  | 1.5 | 1.3
Mon
Tues | 8.8 | 8.7 | 1.2 | 8.6 |  |  |  | 1.4 | 1.2
Tues
Wed | 8.7 | 8.6 | 1.1 | 8.2 |  |  |  | 1.5 | 1.3
Wed
Thur | 9.8 | 9.8 | 1.4 | 8.9 |  |  |  | 1.4 | 1
Thur | 8.7 | 8.7 | 1.2 | 8 |  |  |  | 1.5 | 1.3
Fri | 9.1 | 9.1 | 1.2 | 8.9 |  |  |  | 1.6 | 1.1
Fri | 9.1 | 9 | 1.3 | 8.9 |  |  |  | 1.6 | 1.2
Sat | 8 | 8 | 1.7 | 8.3 |  |  |  | 1.6 | 1.1
Sat | 8.8 | 8.8 | 1.3 | 9 |  |  |  | 1.4 | 1.1
AVG: | 8.91 | 8.87 | 1.28 | 8.59 | #DIV/0! | #DIV/0! | #DIV/0! | 1.53 | 1.2