## SR
FISHWAY STATUS REPORT | [6 empty] | JOHN DAY DAM
Date: | 2010-03-29 | [7 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 03/21-27/2010 | [6 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | Temperature: |  | 44.5714 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.8571 | Ft.
NORTH FISHWAY |  |  | OOS |  | New water up date is 1 April (per Natalie Richards)
≤ 0.5'
Exit hydraulic weirs |  |  |  | Per forebay | Set for forebay >263'
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Entrance differential |  |  |  | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir EW1 |  |  |  | depth (≥ 8') | AVG | #DIV/0!
Entrance weir EW2 |  |  |  | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.1286
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.5357
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.6286
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.25
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 9.1929
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 9.0214
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.55
Submersible traveling screens |  |  | OOS | visual inspect | STSs are scheduled for deployment 3/29-3/31
Turbine trashrack drawdown |  |  | N/A | <1.5', wkly
Vert barrier screen drawdown |  |  | N/A | <1.5', wkly
Spill volume |  |  | OOS | On Seal | Fish spill season starting on 4/10.
Spill pattern |  |  | N/A | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Juvenile passage season is starting on 1 April!
SMF was watered up on 30 March, AM; first fish sample on 4/1.
Operation: | Winter maintenance season ended on 3/29. SMF 24 hrs /7 days biotech coverage starting on 3/31, PM.
All gatewell orifices are open and working properly.
Maintenance:
JDM sealed leaks in the compressed air supply line on 3/30.
SMF AWS valve 111 was reopened on 3/23. No leaks, all AWS pipes are OK.
JDM planning for repainting of faded AWS and drainage pipes in summer (contract.)
OTHER ISSUES:
JOHN DAY
Birds: | See Bird Tab
Avian lines grid phase 2 construction commenced by contractor on 2/1. Six new attachment towers and most lines have been already installed.
All 128 lines are expected to be installed by 9 April.
New construction: JD North ladder's counting station and control weirs contact is in final stage of construction/ testing; water up on 4/6.
Spillway bay 20 flow deflector completed on 3/25. Contractor demobilizing 3/29-4/2. JDS removing bulkheads on 3/26-27.
Maintenance:
South fish turbine # 3 rehab - new plan is under discussion with some internal coordination by JDM underway. Expected contract award this April.
New ETR is March 2011.
Fishways' automation design is in the planning stage with installation activities by JDE (Electrical) starting as soon as all ordered parts are received.
Calibration: Conducted on 3/20. All parameters were within established criteria.
Operations:
All MUs intake trashracks were raked in preparation for fish passage season 3/15-20.
STS camera device without the VBS capability. JDE(Electrical) will be replacing video system with brand new hardware for 2010 season soon.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Research:
Planning and coordinating with contractors for 2010 research season continues.
Normandeau JD bay 20 flow deflector post-construction biological evaluations will take place 4/1-9. Pre-work meeting on 3/29, release pipe installation
on by MidColumbia Inc on 3/30 (sub.) No project support required outside of safe clearance (MZ.)
PNNL crew installed all spillway hydrophones on 3/30. Forebay clusters and powerhouse hydrophones will be installed next, 4/7- 9.
No project support required outside of safe clearance (MZ.)
University of Idaho telemetry crew continues with winter maintenance of lamprey PIT half-duplex antennas. Additionally, they are reinstalling
the adult radio telemetry antennas at both fishways for 2010 adult salmon tracking.
Approved by; Jerry Carroll
Operation Project Manager
John Day Dam

## Birds
S2:
S1:
S3:
P4: Six DCC
P3: Five DCC
P2:
P1:
S4:

## AVGS
John Day:
| Temp: |  | Secchi:
Sun | 44 |  | 5.5
Mon | 44 |  | 6
Tues | 45 |  | 5.5
Wed | 45 |  | 6
Thur | 44 |  | 6
Fri | 44 |  | 6
Sat | 46 |  | 6
AVG: | 44.5714 | AVG: | 5.8571
| N.Ent | EW1 | S.Ent | SE1 | Bay1 | Bay19 | NE1 | NE2 | JBS Diff
Sun | OOS | OOS | 1.2 | 9.1 | 1.6 | 1.1 | 9.4 | 9.2 | 4.6
Sun |  |  | 1.2 | 8.3 | 1.5 | 1.3 | 8.9 | 8.7 | 4.6
Mon |  |  | 1.1 | 8.5 | 1.6 | 1.3 | 9.3 | 9 | 4.6
Mon |  |  | 1.2 | 8.5 | 1.6 | 1.1 | 9.2 | 9.1 | 4.5
Tues |  |  | 1.2 | 8.6 | 1.5 | 1.2 | 9.1 | 9.1 | 4.4
Tues |  |  | 1.1 | 8.6 | 1.6 | 1.1 | 9.4 | 9.3 | 4.6
Wed |  |  | 1 | 8.8 | 1.6 | 1.2 | 9.3 | 9.1 | 4.5
Wed |  |  | 1 | 8.7 | 1.5 | 1.1 | 9.3 | 9.2 | 4.6
Thur |  |  | 1 | 8.5 | 1.5 | 1.2 | 9.4 | 9.1 | 4.5
Thur |  |  | 1.1 | 8.4 | 1.6 | 1.1 | 9.4 | 9.3 | 4.6
Fri |  |  | 1.1 | 8.3 | 1.7 | 1.4 | 9.3 | 9 | 4.6
Fri |  |  | 1.3 | 8.2 | 1.9 | 1.5 | 8.8 | 8.7 | 4.6
Sat |  |  | 1.2 | 8.6 | 1.8 | 1.5 | 8.9 | 8.7 | 4.5
Sat |  |  | 1.1 | 8.4 | 1.8 | 1.4 | 9 | 8.8 | 4.5
AVG: | #DIV/0! | #DIV/0! | 1.1286 | 8.5357 | 1.6286 | 1.25 | 9.1929 | 9.0214 | 4.55