## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: | 2011-04-24 | [8 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 4/17 thru 4/23/2011 | [7 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 46.7143 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 2.7857 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for HIGH forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.4
Entrance weir EW1 |  |  | 0 | depth (≥ 8') | AVG | 9.3857
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.25
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.7857
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.5357
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.55
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 10.2
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 8.9429
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.5571
Submersible traveling screens |  |  | 0 | visual inspect | Next monthly video STS inspection is scheduled for week of 4/25.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | Performed on 4/21. All OK.
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly | Performed on 4/21. All OK.
Spill volume |  |  | 0 | 30% | 30 % until 4/27. Then 30/40 % experimental blocks, changing according to study design
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | In service since March 30. First 24 hrs sample occurred on 4/1/11 and has been occurring daily since.
Maintenance:
3 way gate experienced short failure / disruption early AM on 4/18. The problem was promptly recognized by JD Fisheries and appears to be fixed
as the gate has been working properly since.
PDS screen cleaner repairs and maintenance were completed on 4/11. Auto sweeping six times per day.
PNNL tagging crew started their juvenile salmonids collection at SMF on 4/24. Tagging will commence on 4/25.
Fallbacks | AVG | 97 | MAX | 151 |  | MIN | 67
OTHER ISSUES:
JOHN DAY
Birds: | see bird tab
All 128 avian lines are out of the water and properly tensioned. Four tag lines (furthest downstream) are broken and missing but it is a minor issue.
USDA Animal Control Unit's gull hazing from boats in the JD tailrace started on 4/11. Only small number of gulls occasionally present so far.
New construction: 15 kV tap's installation by contractor (for the North Ladder's future AWS pumps ) is almost complete.
JD Fisheries participating in JDN entrance improvements' design, surveys and inspections. Construction activities are planned of the next year.
BPA approved additional funding for completion of the JD South AWS turbine 3 rehab. A contractor is expect to be mobilizing and starting work
in mid April. ETR is January 2012.
Maintenance:
STS camera device returned to regular service on 4/14 after winter long maintenance / upgrades to its video system. It is a major improvement
and kudos are due to JDE and JDS for excellent in- house redesign and new cameras installation!
Three out of six North AWS pumps are OOS after #3 failed on 4/20, but we are easily meeting all criteria with the remaining three pumps. JDM is
planning to make one spare available in two weeks and then will be repairing the second spare as well.
All six pumps are scheduled for replacement during the upcoming IWW period. (Three pumps currently in service, no spares at this time.)
NE 1 and 2 weirs' LCD display failed and is currently under repairs by JD Electrical. Fisheries crew is measuring weir elevations with a tape.
South Fishway's automation work will be completed soon as the funding is dropped in partial amounts.
MU 11 was dewatered on 4/5, scroll case and draft tube the same day. Fisheries inspection did not detect any fish in either location.
Calibration: Conducted on 4/22; all were within established limits except for NE-1.
Gate well drawdown: Conducted on 4/21; all 48 trashracks/ VBSs were within established limits.
Operations:
Both adult fishways were in regular service during this report period.
JD South entrance weirs N1 &2 old auto control is increasingly unreliable. New PLC automation is planned for final implementation soon.
After a prolonged outage in 2010, the JD trashrack gentry had been repaired. It is now available for service.
STS camera device returned to service on 4/14. Its old / outdated video cameras were replaced with brand new hardware during the winter outage.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Research:
FFU's gull monitoring crew started their observations on 4/11 and will continue them through July.
Planning for 2011 research activities is underway. PNNL crew has already installed all spillway and powerhouse hydrophones, now setting up
computers and testing the monitoring system. They are also setting up their fish collection at JD SMF. The start of PNNL biological evaluations
of TSWs and of comprehensive dam passage monitoring is scheduled for 4/27.
U of I continues with adult lamprey PIT detections and with adult salmonids radiotelemetry tracking at both JD ladders.
Approved by Jerry Carroll
Operation Project Manager
John Day Dam

## FishCounts
John Day 2011
| South | North | South | North | South | North
| ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd
2011-04-17 | 7 | 0 | 0 | 0 | 43 | 14
2011-04-18 | 12 | 6 | 1 | 0 | 27 | 12
2011-04-19 | 16 | 5 | 0 | 0 | 15 | 9
2011-04-20 | 13 | 2 | 0 | 0 | 31 | 10
2011-04-21 | 37 | 5 | 0 | 0 | 18 | 6
2011-04-22 | 24 | 5 | 0 | 0 | 15 | 7
2011-04-23 | 31 | 16 | 0 | 0 | 12 | 7

## Birds
S2:
S1: No birds observed
S3:
P4:
P3:
P2:
P1: NO birds observed
S4:

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 47 |  | 3 |  | 88
Mon | 47 |  | 2.5 |  | 79
Tues | 47 |  | 2.5 |  | 80
Wed | 47 |  | 2.5 |  | 105
Thur | 47 |  | 3 |  | 109
Fri | 46 |  | 3 |  | 67
Sat | 46 |  | 3 |  | 151
AVG: | 46.7143 | AVG: | 2.7857 | AVG | 97
|  |  |  | MAX | 151
|  |  |  | MIN | 67
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 9.9 | 8.8 | 1.2 | 9.2 | 1.3 | 8.6 | 4.6 | 1.4 | 1.5
Sun | 9.9 | 8.8 | 1.2 | 8.6 | 1.5 | 8.5 | 4.6 | 1.5 | 1.6
Mon | 10.2 | 8.7 | 1.3 | 8.9 | 1.4 | 8.5 | 4.5 | 1.5 | 1.6
Mon | 10.4 | 8.9 | 1.2 | 8.9 | 1.5 | 8.5 | 4.5 | 1.6 | 1.7
Tues | 9.1 | 8.3 | 1.4 | 8.3 | 1.3 | 10 | 4.6 | 1.7 | 1.8
Tues | 8.9 | 8.6 | 1.2 | 8.7 | 1.4 | 8.4 | 4.6 | 1.5 | 1.6
Wed | 10.1 | 8.9 | 1.2 | 8.9 | 1.4 | 9.6 | 4.6 | 1.6 | 1.8
Wed | 10.9 | 9.8 | 1.3 | 8.4 | 1.5 | 9.6 | 4.6 | 1.5 | 1.5
Thur | 10.9 | 9.1 | 1.2 | 10.3 | 1.3 | 10 | 4.6 | 1.5 | 1.2
Thur | 10.8 | 9 | 1.2 | 8.3 | 1.4 | 9.8 | 4.5 | 1.4 | 1.3
Fri | 10.7 | 9.7 | 1.3 | 8.7 | 1.4 | 10.3 | 4.5 | 1.5 | 1.7
Fri | 10.4 | 8.9 | 1.3 | 8.4 | 1.4 | 10.9 | 4.5 | 1.6 | 1.3
Sat | 10.9 | 9 | 1.2 | 8.9 | 1.4 | 10 | 4.5 | 1.5 | 1.6
Sat | 9.7 | 8.7 | 1.3 | 8.5 | 1.4 | 8.7 | 4.6 | 1.7 | 1.5
AVG: | 10.2 | 8.9429 | 1.25 | 8.7857 | 1.4 | 9.3857 | 4.5571 | 1.5357 | 1.55