## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: |  | 2012-05-20 | [7 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 5/13 thru 5/19/2012 | [7 empty] | P.O. Box 564
Rufus, Oregon 97050
Phone: 541-506-7860
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 54.2857 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 3.1429 | Ft.
NORTH FISHWAY |  |  |  |  | Three AWS pumps in service (see Operations section below for special info)
Exit differential |  |  | 1 | ≤ 0.5' | at 0.6 ' due to 2 AWS pumps not restarting properly by the auto controls on 5/18
Exit Control weirs |  |  | 0 | Per forebay | Set for HIGH forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.4643
SOUTH FISHWAY |  |  |  |  | Regular three turbine operation with four floating orifices since 5/8/12
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.4929
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 9.35
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.8357
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.5286
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 10.4929
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 10.5571
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.5643
Submersible traveling screens |  |  | 0 | visual inspect
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | 5/10/12 No discrepancies
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly | 5/10/12 No discrepancies
Spill volume |  |  | 0 | 30%/40% | Standard testing started on 4/27, 30/40%, 3 day- blocks will continue through mid July.
Spill pattern |  |  | 0 | per FPP | TWSs in service at bays 18 & 19 since 4/10.
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | SMF in sampling mode since 3/31. Condition/ Index sampling by PSMFC biologists occurring 24/7 through 15 September.
Debris: Light to occasional moderate, mostly tumbleweed and other small sticks/twigs.
PDS screen cleaners in regular service, cycling every 4 hours. |  |  |  |  | Debris at Fish/Debris separator very light.
Maintenance: None; all SMF equipment has been working properly.
Research: Collection of smolts for the 2012 PNNL's tagging (with acoustic tags) commenced on 4/25. PSMFC biologists will assist this intensive fish
collection effort 7 days a week through mid July. PNNL marking crew/ fish surgeons continue with approximately 400- 500 of smolts per day.
Fallbacks | AVG | 79.8571 | MAX | 113 |  | MIN | 65
OTHER ISSUES:
JOHN DAY
Birds: | see bird tab
JD tailrace BRZ Avian Lines repair and improvements' contract was completed in February. After the two previously missing Powerhouse lines were
replaced on 5/14, all 125 lines are properly installed and entire JD avian grid is complete.
USDA gull hazing crew on site since 4/17. Hazing from a boat located just downstream of JD tailrace BRZ will occur 0700-1500 hrs, 7 days a week,
through the end of July. The numbers increase after hazing stops at 1500 hrs, but majority of gulls observed are downstream of the lines.
Operations:
Intermittent outages of two out of three JD North AWS pumps continue; one occurred on 5/14 and another on 5/18 with one pump remaining always in
service uninterrupted. JD Fisheries checking the JDN entrance differential to detect those shut downs, one pump provides insufficient AWS/ differential
of only 0.6'. It takes 2-3 hrs on average for JD Operations to restart the pumps manually with local controls; then they run for a few days just fine.
VFD software/communications have been identified as a culprit and a solution is being discussed with the pumps' contactor. In spite of those outages,
the adult passage through the JD North fishway appears to be good.
JD South fishway is in regular service with three turbines; no problems or issues of any kind.
Gatewell inspection on 5/15 detected juvenile chinook morts at MU13, slot A - 1 mort and 13B- 2 morts. Immediate gatwells drawdown was preformed
on all MU s and a few close to MU 13 were found at 1.5'. Raking the next day, on 5/16 lowered the excessive drawdowns successfully and no more
morts were detected during this report period.
New construction:
A contractor continues installation of the two remaining JD North's AWS pumps, # 5 and 6. However, a systematic problem with bearings on all pumps
is suspected/investigated; # 5 failed its dry test and # 1 is out of service due to high bearing's temps.
Maintenance:
JD STS and orifice camera inspection is scheduled for next week, starting on 5/21.
Gatewell drawdown: 5/15/12. MU slots 7 c, 18b and 16c were at 1.5 and slot 12c was at 1.7. The respective intake trashracks were raked by JDS.
A gatewell drawdown was done after raking and all units were under 1.5.
Calibration: | 2012-05-16 | All in criteria
Research:
Fish counting commenced at both JD Fishways, the South and North on 4/1 and will continue daily, 7 days a week through October.
PNNL commenced their 2012 JD biological evaluations of TSWs and total juvenile passage on 4/27, after the first boat release of fish occurred at
Arlington. The acoustic monitoring/ detections for all JD juvenile fish passage routes will continue 24/7 through 20 July.
PSMFC pikeminnow dam angling/ removal started from JD tailrace deck, on 5/3 and is expected to continue through August. Low catch numbers due
to high river flows and turbid water; fishing is expected to improve later in May and June.
ODFW smallmouth bass survey/ research angling started at JD on 5/7, early AM. Their crew will be fishing at different tailrace and forebay locations
a couple of days a week, through August.
JD Fisheries team continues with safety and security briefings for all new fisheries contract personnel slated to work at our project in 2012.

## FishCounts
John Day 2012
| South | North | South | North | South | North
| ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd
2012-05-13 | 3950 | 4796 | 175 | 163 | 5 | 1
2012-05-14 | 2744 | 2822 | 162 | 132 | 0 | 3
2012-05-15 | 2622 | 2654 | 156 | 112 | 4 | 1
2012-05-16 | 2306 | 3756 | 180 | 208 | 8 | 5
2012-05-17 | 3482 | 3905 | 283 | 200 | 12 | 2
2012-05-18 | 2792 | 2194 | 330 | 169 | 6 | 5
2012-05-19 | 2034 | 1475 | 247 | 172 | 4 | 4

## Velocities
Bay(s) | Velocity (f/s)
0-2 | 2.7692
2 - 4 | 3.3333
4 - 6 | 3.3962
6 - 8 | 3.1579
8 - 10 | 3.0508
10 - 12 | 2.8571
12 - 14 | 3.5294
14 - 16 | 3.2143
16 - 18 | 4.2857

## Birds
SW T2: No birds
SW T3: 6 gulls foraging. SW T4: 129 gulls fly, 53pelicans
SW T1: : No birds .
PH FB: 16 gulls, 15 grebes
PH T1: No birds
PH T2: no birds.
PH T3: 1 gulls fly PH T4: 56 gulls fly
SW FB: 4 gulls resting,

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 52 |  | 3 |  | 113
Mon | 53 |  | 3 |  | 67
Tues | 55 |  | 3 |  | 65
Wed | 54 |  | 3.5 |  | 97
Thur | 55 |  | 3 |  | 72
Fri | 55 |  | 3.5 |  | 67
Sat | 56 |  | 3 |  | 78
AVG: | 54.2857 | AVG: | 3.1429 | AVG | 79.8571
|  |  |  | MAX | 113
|  |  |  | MIN | 65
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 11 | 10.9 | 1.3 | 8.2 | 1.6 | fixed | 4.5 | 1.8 | 1.5
Sun | 10.4 | 10.3 | 1.6 | 9.1 | 1.6 | fixed | 4.6 | 2 | 1.5
Mon | 9.8 | 9.6 | 1.4 | 9.2 | 1 | fixed | 4.6 | 2 | 1.5
Mon | 10.7 | 10.7 | 1.5 | 9.4 | 1.5 | fixed | 4.5 | 1.8 | 1.4
Tues | 9.6 | 9.6 | 1.7 | 8.7 | 1.6 | fixed | 4.6 | 1.8 | 1.6
Tues | 10.7 | 10.7 | 1.4 | 9.7 | 1.6 | fixed | 4.6 | 1.6 | 1.8
Wed | 10.3 | 10.4 | 1.4 | 10 | 1.5 | fixed | 4.5 | 1.9 | 1.4
Wed | 10.6 | 10.7 | 1.4 | 8.8 | 1.5 | fixed | 4.6 | 1.7 | 1.8
Thur | 10.2 | 10.4 | 1.7 | 9.4 | 1.5 | fixed | 4.6 | 1.9 | 1.5
Thur | 11.4 | 11.6 | 1.6 | 9.7 | 1.6 | fixed | 4.6 | 1.9 | 1.4
Fri | 11.5 | 11.7 | 1.3 | 10.3 | 1.6 | fixed | 4.6 | 1.8 | 1.4
Fri | 9.1 | 9.3 | 1.6 | 9.7 | 0.6 | fixed | 4.5 | 1.9 | 1.6
Sat | 11.1 | 11.3 | 1.5 | 9.6 | 1.6 | fixed | 4.6 | 1.8 | 1.5
Sat | 10.5 | 10.6 | 1.5 | 9.1 | 1.7 | fixed | 4.5 | 1.8 | 1.5
AVG: | 10.4929 | 10.5571 | 1.4929 | 9.35 | 1.4643 | na | 4.5643 | 1.8357 | 1.5286