## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: | 2010-06-20 | [8 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 6/13 thru 6/19/2010 | [7 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 58.8571 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 2.3571 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.3' ± 0.1' | Changed from normal 1.0' to 1.3' for shad passage on 5/30
Entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.4
Entrance weir EW1 |  |  | 0 | depth (≥ 8') | AVG | 10.15
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.3' ± 0.1' | Changed from normal 1.0' to 1.3' for shad passage on 5/30
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.4143
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.2286
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.65
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.6857
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 9.6786
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 9.2
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 1.6857
Submersible traveling screens |  |  | 0 | visual inspect | Inspected week of 5/24, no problems with STSs or orifices were found.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly
Spill volume |  |  | 0 | 30/40% | 30/40% according to experimental TSW block study design
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Juvenile passage season started on 1 April and will continue through 30 November.
SMF was watered up on 30 March, AM; first fish sample by PSMFC on 4/1. It will remain in sampling mode through 15 September.
Operation: | 24 hrs /7 days biotech coverage started on 3/31, will continue through 15 September.
Elevated juvenile salmonids mortality ended on 5/19 and continues to be low/normal (less than 0.5%)
Maintenance:
Repainting of faded AWS pipes was moved out to FY '11.
All SMF equipment in service and working properly. 2-way gate operated manually every 2 hours to prevent sticking.
New heat pump for SMF building was installed 5/24, just in time for coming summer!
Research: PNNL's research activities re-started for summer component after a two weeks recess on 6/11; first summer release occurred on 6/13.
Smolt collecting, marking at SMF and releasing at Roosevelt will continue through mid July.
The summer component of TSW evaluations will restart with collection of summer smolts on 6/12 and will continue through mid July.
USGS is collecting juvenile lamprey for their tagging study.
Adult Fallback Count: |  | Maximum: | 221 | Minimum: | 116 | Average: | 152.1429
OTHER ISSUES:
JOHN DAY
Birds: | See bird tab
The previous week's high gull numbers appear to be due to peak juvenile lamprey migration as the avian activities declined precipitously this week
(fewer lamprey.)
USDA continues successful hazing from boats inside tailrace BRZ, two shifts per day, from 0600 to 2000 hrs; only small number of gulls is observed
within BRZ while hazing is underway. Some hazing effort is being transferred to TD due to higher gull number there.
Avian lines grid's phase 2 construction was completed on 4/9. All 128 primary lines have been installed but two broke due to warning streamers
cutting into them. They are not possible to re-attach until the next year; the loss of coverage area is minimal (terminal lines.)
PSMFC pikeminnow anglers started fishing from JD tailrace deck on 5/17 and caught 378 fish total by 6/07.
New construction: 15 kV tap's installation by contractor (for the North Ladder's future AWS pumps ) is ongoing.
Maintenance:
South fish turbine # 3 rehab - new plan is under discussion with some internal coordination by JDM underway. Contract has been awarded with new
RTS in December 2011.
Fishways' automation equipment is being currently installed by JDE at South fishway; expected completion is this August.
Two out of six North AWS pumps are currently OOS due to mechanical failures; one bad motor, another bad gear box. One failed pump will return back
to service soon but bad motor may take longer to repair (winter maintenance ?) Three good AWS pumps are in service with one spare available at this
time.
Calibration: Conducted on 6/12. All parameters were within established criteria. Gatewell drawdown was done 6/12, all are within established limits.
Operations:
South and North adult fishways are both in regular service, both are meeting all FPP criteria.
Problems with North's crowder and window brush continue; COR is involved in planning for repairs by a contractor in the end of June. Window was
cleaned by JDS manually on 6/1 and it will continue until the auto brush is repaired.
All MUs intake trashracks were raked the week of 6/7. Low debris' levels due to drought conditions this year.
All STS and orifices were video inspected week of 5/24; no problems were detected.
STS camera device without the VBS capability. JDE(Electrical) will be replacing video system with brand new cameras/hardware soon.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Research:
PNNL's TWS' evaluation re-started its summer activities after two weeks recess on 6/11; first summer release of marked smolts occurred on 6/13.
PNNL crew will continue collecting smolts, marking them at SMF and releasing from boats at Roosevelt through mid July.
University of Idaho telemetry crew completed installation of lamprey PIT half-duplex antennas by 4/1; they are monitoring lamprey passage now.
CRITFC's monitoring of adult lamprey passage through picketed leads at JD North counting station continues.
Also, U of I adult salmonids tracking antennas were installed at both ladders this spring and are currently monitoring radio tagged fish passage.
Approved by; Jerry Carroll
Operation Project Manager
John Day Dam

## FishCounts
| South | North | South | North | South | North | South | North | South | North
Date | ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd | Sockeye | Sockeye | Lamprey | Lamprey
2010-06-13 | 710 | 307 | 55 | 41 | 34 | 48 | 155 | 379 | 4 | 0
2010-06-14 | 776 | 517 | 92 | 114 | 30 | 77 | 222 | 700 | 0 | 1
2010-06-15 | 1049 | 446 | 170 | 74 | 71 | 64 | 654 | 966 | 1 | 0
2010-06-16 | 864 | 569 | 101 | 91 | 76 | 139 | 773 | 1523 | 1 | 0
2010-06-17 | 701 | 392 | 154 | 90 | 50 | 73 | 944 | 1777 | 0 | 0
2010-06-18 | 640 | 353 | 60 | 50 | 42 | 106 | 959 | 1630 | 0 | 0
2010-06-19 | 746 | 446 | 96 | 60 | 41 | 70 | 1031 | 1837 | 0 | 0

## Birds
S2:
S1:
S3:
P4: 72 grebe, 40 gulls
P3:10 gulls
P2:
P1:
S4:4 grebe

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 58 |  | 2.5 |  | 138
Mon | 58 |  | 2.5 |  | 118
Tues | 59 |  | 2.5 |  | 221
Wed | 59 |  | 2.5 |  | 141
Thur | 59 |  | 2.5 |  | 127
Fri | 59 |  | 2 |  | 116
Sat | 60 |  | 2 |  | 204
AVG: | 58.8571 | AVG: | 2.3571 | AVG | 152.1429
|  |  |  | MAX | 221
|  |  |  | MIN | 116
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 9.3 | 9 | 1.4 | 8.2 | 1.4 | 9.9 | 4.6 | 1.5 | 1.8
Sun | 9.2 | 9.1 | 1.5 | 8.1 | 1.5 | 9.8 | 4.5 | 1.6 | 1.8
Mon | 9.7 | 9.3 | 1.6 | 8.2 | 1.3 | 10.5 | 4.65 | 1.9 | 1.4
Mon | 9.5 | 9 | 1.4 | 8.1 | 1.4 | 10.1 | 4.5 | 1.7 | 1.8
Tues | 9.8 | 9.2 | 1.4 | 8.4 | 1.4 | 10.1 | 4.7 | 1.7 | 1.7
Tues | 9.6 | 8.9 | 1.4 | 8.1 | 1.4 | 10.2 | 4.5 | 1.6 | 1.8
Wed | 9.6 | 9 | 1.5 | 8.1 | 1.4 | 10.3 | 4.6 | 1.7 | 1.9
Wed | 9.8 | 9.4 | 1.3 | 8.2 | 1.4 | 10.3 | 4.5 | 1.5 | 1.7
Thur | 10 | 9.5 | 1.3 | 8.6 | 1.4 | 10.4 | 4.5 | 1.5 | 1.5
Thur | 10 | 9.4 | 1.4 | 8.5 | 1.4 | 10.4 | 4.6 | 1.6 | 1.8
Fri | 10.3 | 9.5 | 1.4 | 8.6 | 1.3 | 10.3 | 4.6 | 1.7 | 1.6
Fri | 10 | 9.2 | 1.5 | 8 | 1.4 | 10.2 | 4.6 | 1.8 | 1.7
Sat | 9.2 | 9.2 | 1.3 | 8.1 | 1.5 | 9.6 | 4.5 | 1.7 | 1.5
Sat | 9.5 | 9.1 | 1.4 | 8 | 1.4 | 10 | 4.6 | 1.6 | 1.6
AVG: | 9.6786 | 9.2 | 1.4143 | 8.2286 | 1.4 | 10.15 | 4.5679 | 1.65 | 1.6857