## SR
FISHWAY STATUS REPORT | [7 empty] | JOHN DAY DAM
Date: 08/01/10 | [9 empty] | JD/WC Project-Fisheries
Inspection Period: 07/25 - 07/31/2010 | [9 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 13 | Temperature: |  | 68.28 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: |  | 5.48 | FT.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.3' ± 0.1' | It hasn't been changed to salmon's 1.0' yet, pending and will next week.
Entrance differential |  |  | 0 | 1.0' - 2.0' | 1.35
Entrance weir EW1 |  |  | 2 | depth (≥ 8') | 8.26 | Out @ 7.9, 7.8 |  | Due to low tailrace in summer.
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Changed back from shad's 1.3 ' to salmon passage's 1.0 ' on 7/26.
South entrance differential |  |  | 1 | 1.0' - 2.0' | 1.24 | Out @ 0.8 |  | Due to new control system's installation work
Entrance weir SE1 |  |  | 1 | depth (≥ 8') | 8.59 | Out @, 7.1 |  | Due to new control system's installation work
Collection channel velocity |  |  | 0 | 1.5 - 4 fps |  | did not measure velocity
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | 1.59
N. Entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | 1.38
Entrance weir NE1 |  |  | 2 | depth (≥ 8') | 8.05 | Out @, 7.9, 7.3 |  | Due to old system's problems, new system on the way!
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | 8.86 |  |  | (Activation soon, possibly in August.)
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | 4.56
Submersible traveling screens |  |  | 0 | visual inspect | last camera inspection week of 7/19.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | Low debris period so July raking of trashracks postponed to August. Trashracks are clean.
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly
Spill volume |  |  | 0 | 30% 24 hrs
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
SMF was changed to bypass on 7/29 at 1300 hours to protect migrating smolts from excessive stress when river temperature is above 70 ⁰F.
Reduced sampling, smolt condition only will be conducted twice a week for 6 hours, Mondays and Thursdays, until river temperature drops below 70 ⁰F.
SMF will remain in sampling mode through 15 September. Then, it will operate in bypass for full flow PIT detection through November 30.
Operation: | 24 hrs /7 days biotech coverage started on 3/31, will continue through 15 September.
Elevated juvenile salmonids mortality ended on 5/19 and continues to be low/normal (less than 0.5%)
Maintenance:
Repainting of faded AWS pipes was moved out to FY '11.
All SMF equipment in service and working properly. 2-way gate is sticking and will be fixed after September 15.
Research: PNNL's research will be completed on 7/20. Last fish collection at SMF occurred on 7/15 and last release at Roosevelt was on 7/17.
No research activities of any kind are occurring at this time.
Adult Fallback Count: |  | Maximum: | 181 | Minimum: | 124 | Average: | 152.29
OTHER ISSUES:
JOHN DAY
Birds: | See bird tab
Very few gulls are being observed at JD tailrace BRZ at this time.
USDA continued successful hazing from boats inside tailrace BRZ, two shifts per day, from 0600 to 2000 hrs; only small number of gulls is observed
within BRZ while hazing is underway. Hazing season ended on 7/27.
PSMFC pikeminnow anglers continue fishing from JD tailrace deck , they had great week catching 359 fish for the season total of 1,564, through 8/1.
New construction: 15 kV tap's installation by contractor (for the North Ladder's future AWS pumps ) is ongoing.
Maintenance:
South fish turbine # 3 rehab - new plan is under discussion with some internal coordination by JDM underway. Contract has been awarded with new
RTS in December 2011.
Fishways' automation equipment is being currently installed by JDE at South fishway; expected completion is early August.
Two out of six North AWS pumps are currently OOS due to mechanical failures; one bad motor, another bad gear box. One failed pump will return back
to service soon but bad motor may take longer to repair (winter maintenance ?) Three good AWS pumps are in service with one spare available at this
time.
MU11 was dewatered on 7/26 -27, Only small number of resident fish were found, 2 crappies and 1 cat in scroll case, 1 sturgeon, 5 cats in draft tube.
All fish were transported and released back into the river in excellent condition.
Calibration: Conducted on 7/29. All parameters were within established criteria. Gatewell drawdown was done 7/30, all are within established limits.
Operations:
South and North adult fishways are both in regular service and are meeting all FPP criteria.
Summer spill operation started on 7/21. TSWs were closed and spill pattern was changed to bulk through North bays (Washington shore.)
Problems with North's crowder and window brush continue; COR is involved in planning for repairs by a contractor in August. Window is being
cleaned by JDS manually until the auto brush is repaired.
All MUs intake trashracks were raked the week of 6/7. Low debris' levels due to drought conditions this year so July raking was postponed to August.
All STS and orifices were video inspected week of 7/19; one STS had bad mesh and was replaced immediately with spare. June's inspection delayed
due to high flows, but smolt sampling results at SMF have been OK so no big issue.
STS camera device without the VBS capability. JDE(Electrical) will be replacing video system with brand new cameras/hardware soon.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Research:
PNNL's TWS' 2010 evaluation was completed on 7/20. Last fish release occurred at Roosevelt on 7/17. Their crew will start removing equipment and
clean up at the forebay deck in August.
Umatilla tribe continues their adult lamprey trapping at both JD counting stations, low numbers captured so far.
CRITFC continues with monitoring of adult lamprey passage through picketed leads at JD North counting station.
U of I continues with adult lamprey PIT detections and with adult salmonids radiotelemetry tracking at both JD ladders.
Approved by; Jerry Carroll
Operation Project Manager
John Day Dam

## FishCounts
| South | North | South | North | South | North | South | North | South | North
Date | ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd | Sockeye | Sockeye | Lamprey | Lamprey

## Birds
S2:
S1:22 pelicans
S3:
P4:28 grebes, 17 gulls, 6 pelicans
P3:
P2:
P1:
S4:22 gulls, 1 pelican

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 71 |  |  |  | 219
Mon | 69 |  | 5.5 |  | 219
Tues | 70 |  | 5 |  | 199
Wed | 70 |  | 6 |  | 177
Thur | 70 |  | 6 |  | 119
Fri | 70 |  | 6
Sat | 70 |  | 6
AVG: | 70 | AVG: | 5.75 | AVG | 186.6
|  |  |  | MAX | 219
|  |  |  | MIN | 119
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 8 | 8.7 | 1.6 | 8.1 | 1.4 | 8.4 | 4.7 | 1.6 | 1.2
Sun | 7.8 | 8.9 | 1.2 | 8.4 | 1.5 | 8.9 | 4.5 | 1.5 | 1.3
Mon | 7.9 | 9.1 | 2 | 8.4 | 1.3 | 7.9 | 4.5 | 1.7 | 1.9
Mon | 9 | 8.7 | 1.7 | 8.1 | 1.5 | 8.2 | 4.6 | 2 | 1.8
Tues | 8.4 | 8.9 | 1.5 | 8.4 | 1.4 | 8.2 | 4.5 | 1.6 | 1.7
Tues
Wed | 8.6 | 8.8 | 1.3 | 8.6 | 1.4 | 8.8 | 4.6 | 1.7 | 1.4
Wed | 8.4 | 8.3 | 1.5 | 8.1 | 1.5 | 8.4 | 4.5 | 1.6 | 1.3
Thur | 8.4 | 8.6 | 1.4 | 8.2 | 1.3 | 8.3 | 4.5 | 1.9 | 1.5
Thur | 8.5 | 8.7 | 0.8 | 9.5 | 1.4 | 8.7 | 4.7 | 1.5 | 1.4
Fri | 8.6 | 8.4 | 1.6 | 8 | 1.3 | 8.1 | 4.7 | 1.9 | 1.7
Fri | 8.4 | 8.5 | 1.4 | 8.3 | 1.5 | 8.1 | 4.6 | 1.7 | 1.5
Sat | 8.5 | 8.5 | 1.3 | 7.1 | 1.4 | 7.3 | 4.5 | 1.9 | 1.5
Sat | 9.2 | 9.1 | 1.2 | 8.1 | 1.3 | 8.1 | 4.6 | 1.6 | 1.2
AVG: | 8.4385 | 8.7077 | 1.4231 | 8.2538 | 1.4 | 8.2615 | 4.5769 | 1.7077 | 1.4923