## SR
FISHWAY STATUS REPORT | [5 empty] | JOHN DAY DAM
Date: 12/07/2009 | [7 empty] | JD/WC Project-Fisheries
Inspection Period:11/29 - 12/05/2009 | [7 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541-506-3800
Fishway inspections twice daily through November and then once a day in winter.
John Day Dam |  | Inspections | Criteria | Total Number of Inspections: |  | 9 | Temperature: |  | 49.8571 | F
|  | Out of Criteria | Limit | Comments |  |  | Secchi: | 6 | Ft.
NORTH FISHWAY |  |  |  | North ladder dewatered since 11/16 and it remain OOS until mid March '10.
Exit differential |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1'
Entrance differential |  | 0 | 0
Entrance weir EW1 |  | 0 | depth (≥ 8')
Entrance weir EW2 |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  | 0 | ≤ 0.5'
Hydraulic weir positions |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1'
South entrance differential |  | 0 | 1.0' - 2.0' | AVG | 1.2643
Entrance weir SE1 |  | 0 | depth (≥ 8') | AVG | 8.4857
Collection channel velocity |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  | 0 | 1.0' - 2.0' | AVG | 1.7429
N.entrance PH(Bay 19)differential |  | 0 | 1.0' - 2.0' | AVG | 1.4929
Entrance weir NE1 |  | 0 | depth (≥ 8') | AVG | 9.1214
Entrance weir NE2 |  | 0 | depth (≥ 8') | AVG | 8.9643
JUVENILE PASSAGE
Forebay/bypass conduit differential |  | 0 | 4.0' - 5.0' | AVG | 4.55
Submersible traveling screens |  | 0 | visual inspect | Monthly inspection schedule
Turbine trashrack drawdown |  | 0 | <1.5', wkly
Vert barrier screen drawdown |  | 0 | <1.5', wkly
Spill volume |  | 0 | 30%, 24hr
Spill pattern |  | 0 | per FPP
Turbine Unit Priority |  | 0 | per FPP
Turbine 1% Efficiency |  | 0 | per FPP
SMOLT MONITORING FACILITY
SMF was dewatered on 11/30, AM. It will remain OOS until 1 April '10.
Operation: | 2009 Sampling season ended at 0700 on 9/15. SMF was in bypass and manned 16 hours per day for full flow PIT tag detection from 9/15
through 11/30.
Maintenance:
All flushing/supply water pipes and valves were winterize by Fisheries and JDM crews by 12/4.
JDM planning for repainting of all flushing water supply and drainage pipes in March 2010.
Cleaning and painting of FDS completed. JDM (Mechanical) repair of the two way gate rotation problem completed on 11/18.
OTHER ISSUES:
JOHN DAY
Birds:
Around 50 gulls and 20 grebes in forebay. 200 - 300 gulls, 25 - 50 cormorants, and 15 - 30 mergansers in tailrace.
New and improved, 2010 tailrace avian lines grid design/ planning by Portland District's engineering team underway. Mr. Mackintosh is POC.
New construction: JD North ladder's counting station and control weirs overhaul/ improvements' work started as planned on 17 November,
, a day after early dewatering on 16 November 2009. All construction activities to be completed before 3/15/2010.
Maintenance:
South fish turbine # 3 rehab ongoing - new plan is under discussion with some internal work by JDM underway. New ETR is 1 March 2011.
The remaining two turbines will be completed by the end of FY 2012, one after another.
Fishways' automation design is in the planning stage with installation activities by JDE (Electrical) starting in November '09.
Calibration: | Conducted 11/28 with all parameters within established limits.
Gatewell drawdown checked 11/28. All within criteria.
Operations:
North ladder was dewatered on 11/16. It went well with only small number of fish pushed downstream/handled by Fisheries personnel.
MUs intake trashracks rake's repair completed on 10/29. In service and ready to go for 2010 season!
STS camera device without the VBS capability. JDE(Electrical) will be fixing/ replacing entire video system with brand new hardware for 2010 season.
New underwater/ replacement camera was tested on 8/20 and what an improvement over the outdated/old technology! Four more will be procured
soon. Waiting for vendor's completion of the five cameras system's design before final procurement.
All remaining fishways' passage equipment is working well and fully meeting FPP criteria.
Planning for winter fishway dewaterings and maintenance activities underway.
Research:
Planning meeting for 2010 research, moderated by Portland's Bios was held at JD on 11/17. A large hydroacoustic smolt tracking/passage study (PNNL)
will take place at JD and its impacts will need to be coordinated with management and maintenance crews . However, most of its hardware is already in
place and therefore, the hydroacoustic equipment installation in March '10 will be similar to one in '09; only moderate project impact is expected.
PNNL will soon submit a detailed installation/research plan for the project's review and approval.
University of Idaho telemetry crew continues with weekly downloading of adult lamprey PIT tag data.
Approved by Glen Smith, OPM
John Day Lock and Dam

## PIT Tag Detections
Fish Tag ¦---Release----¦ ¦------------Detection-------------¦
Tag-ID Type Site Site Date First Last Records (Count)
-----------------------------------------------------------------------------------------------------
3D9.1C2CEB5201 Hat. Summer Chinook YAKIM1 NATCHR 06/12/09 11/01/09 11/01/09 4 (4)
3D9.1BF26B1472 Wild Summer Steelhead WENATR WENATR 10/08/07 11/01/09 11/01/09 4 (4)
3D9.1C2C5CED41 Hat. Fall Chinook DWOR SNAKE3 05/22/08 11/02/09 11/02/09 4 (4)
3D9.1BF26BFFD2 Wild Summer Steelhead LGR LGRRBR 05/06/08 11/02/09 11/02/09 4 (4)
3D9.257C65A3E9 Hat. Summer Steelhead IRRI PENP 04/26/07 11/03/09 11/03/09 4 (4)
3D9.1C2CC82C9F Summer Chinook RIS RI2BYP 07/25/09 11/06/09 11/06/09 4 (4)
3D9.1C2CDC78C3 Summer Chinook RIS RI2BYP 07/23/09 11/07/09 11/07/09 4 (4)
3D9.1C2C4F1AC0 Wild Winter Steelhead 15MILC 15MILC 05/13/08 11/07/09 11/07/09 4 (4)
3D9.1BF2764670 Hat. Summer Steelhead LGR LGRRBR 05/26/08 11/09/09 11/09/09 4 (4)
3D9.1C2C40630E Hat. Summer Steelhead IRRI WALH 04/26/08 11/10/09 11/10/09 4 (4)
3D9.1C2C65A003 Wild Summer Steelhead LMN LMNBYP 04/23/08 11/10/09 11/10/09 4 (4)
3D9.1BF2408535 Hat. Summer Steelhead LGR LGRRBR 04/30/07 11/11/09 11/11/09 4 (4)
3D9.1BF26F272F Wild Summer Steelhead LGR LGRRBR 04/28/08 11/11/09 11/11/09 4 (4)
3D9.1BF2551673 Hat. Coho YAKIM1 YAKIM2 07/27/07 11/12/09 11/12/09 4 (4)
3D9.1C2CF0D499 Hat. Fall Chinook YAKIM1 YAKIM1 04/24/09 11/12/09 11/12/09 4 (4)
3D9.1C2D0FCE39 Wild Summer Steelhead LGR LGRRRR 06/11/09 11/12/09 11/12/09 4 (4)
3D9.1BF26F6279 Hat. Summer Steelhead LGR LGRRBR 05/12/08 11/12/09 11/12/09 4 (4)
3D9.1C2CDC8D01 Summer Chinook RIS RI2BYP 07/21/09 11/13/09 11/13/09 4 (4)
3D9.1C2CF80CB8 Hat. Summer Chinook YAKIM1 NATCHR 06/12/09 11/13/09 11/13/09 4 (4)
3D9.1C2CC7FD65 Summer Chinook RIS RI2BYP 07/20/09 11/13/09 11/13/09 4 (4)
3D9.1C2CDC89F7 Summer Chinook RIS RI2BYP 07/31/09 11/14/09 11/14/09 4 (4)
3D9.1BF22EC2A3 Hat. Summer Steelhead LGR LGRRBR 05/07/07 11/14/09 11/14/09 3 (3)
3D9.1C2CDC83D8 Summer Chinook RIS RI2BYP 08/03/09 11/15/09 11/15/09 4 (4)
3D9.1C2C8080C7 Hat. Summer Steelhead HAGE YANKFK 05/12/08 11/16/09 11/16/09 4 (4)
3D9.1C2CC82FA6 Summer Chinook RIS RI2BYP 07/23/09 11/16/09 11/16/09 4 (4)
3D9.1C2CEFD4FB ORPHAN -- Data Not Available -- 11/17/09 11/17/09 4 (4)
3D9.1BF26B619D Hat. Summer Steelhead LGR LGRRBR 05/19/08 11/17/09 11/17/09 4 (4)
3D9.1BF26C348D Hat. Summer Steelhead LGR LGRRBR 04/28/08 11/18/09 11/18/09 4 (4)
3D9.1BF237F938 Hat. Chinook LGR LGRRTR 10/29/07 11/19/09 11/19/09 4 (4)
3D9.1C2C8B22F1 Hat. Summer Steelhead HAGE SAWTRP 04/18/08 11/19/09 11/19/09 4 (4)
3D9.1BF26C5CB7 Hat. Summer Steelhead LGR LGRRBR 05/05/08 11/20/09 11/20/09 3 (3)
3D9.1C2C85875F Hat. Summer Steelhead HAGE SAWTRP 04/17/08 11/20/09 11/20/09 4 (4)
3D9.1C2CDC5487 Summer Chinook RIS RI2BYP 07/25/09 11/21/09 11/21/09 4 (4)
3D9.1C2CEB63E3 Hat. Summer Chinook YAKIM1 NATCHR 06/12/09 11/21/09 11/21/09 4 (4)
3D9.1C2CFEAD9A Wild Fall Chinook UMAR UMAR 07/20/09 11/21/09 11/21/09 4 (4)
3D9.1C2C4024F2 Hat. Summer Steelhead IRRI LSHEEF 04/01/08 11/22/09 11/22/09 4 (4)
3D9.1C2C4C21CE Hat. Summer Steelhead IRRI LSHEEF 04/01/08 11/22/09 11/22/09 4 (4)
3D9.1BF2795179 Hat. Summer Steelhead LGR LGRRBR 05/26/08 11/23/09 11/23/09 4 (4)
3D9.1C2CC56059 Summer Chinook RIS RI2BYP 07/29/09 11/23/09 11/23/09 4 (4)
3D9.1BF26C5C49 Hat. Summer Steelhead LGR LGRRBR 05/05/08 11/25/09 11/25/09 4 (4)
3D9.1C2CC7C09B Summer Chinook RIS RI2BYP 08/10/09 11/25/09 11/25/09 4 (4)
3D9.1C2D144FAE Hat. Fall Chinook DWOR SNAKE3 06/04/09 11/26/09 11/26/09 3 (3)
3D9.1C2CC55E95 Summer Chinook RIS RI2BYP 08/06/09 11/26/09 11/26/09 4 (4)
3D9.1BF2509052 Hat. Summer Steelhead LGR LGRRBR 05/21/07 11/27/09 11/27/09 4 (4)
3D9.1C2D2CA56A Summer Steelhead BONAFF BONAFF 08/19/09 11/27/09 11/27/09 4 (4)
3D9.1C2CEEA7C5 Hat. Summer Chinook YAKIM1 NATCHR 06/12/09 11/28/09 11/28/09 4 (4)
3D9.1C2D07DFFA Chinook BONAFF BONAFF 09/17/09 11/29/09 11/29/09 4 (4)
3D9.1C2D07E72E Hat. Summer Steelhead BONAFF BONAFF 09/30/09 11/29/09 11/29/09 4 (4)
3D9.1BF26F563A Hat. Summer Steelhead LGR LGRRBR 05/12/08 11/30/09 11/30/09 4 (4)
-----------------------------------------------------------------------------------------------------
There have been 49 tags First Detected This Month at JDJ.

## Quagga ZM flow chart
Dreissenid Mussel Control for The Dalles and John Day Dam
Research and data collection | Problem Identification and Evaluation | Alternative Development and Evaluation | Implementation
PSMFC report; Bonneville Division Plan
COE ERDC
COE ERDC
Bureau of Reclamation
RNT Consulting
Site visit
Review planned actions
Recommended alternatives
Selected alternatives
Funding
Schedule
Install
Internet search
Consulting firm; habitat, water quality, CADD
Summarize findings to COE, outline path, report
Internal alternative treatments, Project involvement
Post Evaluation
Cross check results
Internal evaluation
Prioritize
Feasibility

## AVGS
John Day:
| Temp: |  | Secchi:
Sun | 50 |  | 6
Mon | 50 |  | 6
Tues | 50 |  | 6
Wed | 50 |  | 6
Thur | 50 |  | 6
Fri | 50 |  | 6
Sat | 49 |  | 6
AVG: | 49.8571 | AVG: | 6
| N.Ent | EW1 | S.Ent | SE1 | Bay1 | Bay19 | NE1 | NE2 | JBS Diff
Sun |  |  | 1.4 | 8.4 | 1.8 | 1.5 | 9.6 | 9 | 4.6
Sun |  |  | 1.2 | 8.3 | 1.7 | 1.5 | 9 | 8.8 | 4.6
Mon |  |  | 1.2 | 8.9 | 1.6 | 1.7 | 9.1 | 9 | 4.6
Mon |  |  | 1.3 | 8.7 | 1.7 | 1.4 | 9.2 | 8.9 | 4.5
Tues |  |  | 1.3 | 8.2 | 1.9 | 1.6 | 8.9 | 8.8 | 4.5
Tues |  |  | 1.4 | 8.3 | 1.7 | 1.4 | 9.3 | 9.2 | 4.5
Wed |  |  | 1.2 | 8.4 | 1.8 | 1.6 | 8.8 | 8.8 | 4.6
Wed |  |  | 1.2 | 8.6 | 1.7 | 1.5 | 9 | 9 | 4.6
Thur |  |  | 1.4 | 8.4 | 2 | 1.5 | 8.7 | 8.8 | 4.5
Thur |  |  | 1.3 | 8.5 | 1.6 | 1.5 | 9 | 8.9 | 4.5
Fri |  |  | 1.1 | 8.5 | 1.8 | 1.4 | 9.2 | 9 | 4.5
Fri |  |  | 1.4 | 8.5 | 1.8 | 1.4 | 9.4 | 9.2 | 4.5
Sat |  |  | 1.1 | 8.6 | 1.8 | 1.6 | 9.1 | 9 | 4.6
Sat |  |  | 1.2 | 8.5 | 1.5 | 1.3 | 9.4 | 9.1 | 4.6
AVG: | #DIV/0! | #DIV/0! | 1.2643 | 8.4857 | 1.7429 | 1.4929 | 9.1214 | 8.9643 | 4.55