## SR
FISHWAY STATUS REPORT | [6 empty] | JOHN DAY DAM
Date: |  | 2012-12-11 | [6 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 12/02 thru 12/08/2012 | [6 empty] | P.O. Box 564
Rufus, Oregon 97050
Phone: 541-506-7860
One inspection per day since 12/1; additional monitoring via PLC displays located in fisheries office.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 7 | Temperature: |  | 49.1429 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 4.7857 | Ft.
NORTH FISHWAY |  |  |  |  | Dewatered/ OOS since 11/5 |  | ETR is mid March 2013.
Exit differential |  |  | OOS | ≤ 0.5'
Exit Control weirs |  |  | OOS | HIGH
Count station differential |  |  | OOS | ≤ 0.3'
Weir crest depth |  |  | OOS | 1.3' ± 0.1'
Entrance differential |  |  | OOS | 1.0' - 2.0' | AVG | #DIV/0!
SOUTH FISHWAY |  |  |  |  | Scheduled for 2 weeks dewatering/ maintenance outage in late January 2013
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | MID | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.3' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.2571
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 9.5286
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG | 3.15
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.7857
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.3286
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 8.0714
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 8.0571
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.6143
Submersible traveling screens |  |  | 0 | visual inspect
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | Inspected weekly. Trashracks are raked immediately if differential is above 1.5'
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly | No discrepancies
Spill volume |  |  | None | per FPP
Spill pattern |  |  | None | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: |  | Closed for the winter
JBS in regular service for the kelt migrants' protection through 12/15. All STSs will be removed from gatewells by JD Structural crew starting on 12/17.
Debris: | Gatewells cleaned of debris on 12/04/12
Maintenance: Winterization of all flushing pipes/valves by JD Fisheries crew completed. Planning for winter maintenance/PM activities continues.
JD scoping for the SMF CCTV replacement; the original system installed in 1998 is barely usable and its components have been failing frequently.
Research: None
OTHER ISSUES:
JOHN DAY
Birds: | see web site
123 avian lines are properly installed; two are currently missing after breaking in June.
Planning for reinstallation of all lines before the 2013 passage season underway.
Operations:
2012 fish passage season ended on 11/30. Winter maintenance planning underway.
JD North Fishway continues OOS; its entrance improvements' construction activities by Slayden underway. ETR is mid March.
JD South fishway in regular service with all three AWS turbines and is meeting all FPP criteria.
JBS in regular service for the kelt migrants' protection through 12/15. All STSs will be removed from gatewells by JD Structural crew starting on 12/17.
New construction:
Contractor / Construction Office planning for bringing of all 6 JDN AWS pumps into service soon. ETR is mid March.
Slayden continues with the second year of JD North entrance improvements.
Maintenance:
MU intake raking crane returned to service on 12/5. Kudos to JD Mechanical for accomplishing its lengthy/difficult clutch replacement/repairs!
November STS camera inspection was completed by 11/29. One STS found with slightly damaged mesh; it was repaired on the spot and returned to
service the same day.
JD Fisheries detected malfunction of MU 1 orifices on 12/8. JD Ops identified failed selsyn, which was fixed on 12/10.
Gatewell draw down: 12/6/2012. All gatewells were within criteria.
Calibration: | 2012-11-30 | All JD Fishways' PLCs/ water level sensors were within 0.3' margin of error.
Research:
No fish research or fish counting taking place at JD since October 31.
JD Fisheries involved in PDTs for JD South lamprey trap and in JD North LPS designs.
JD Fisheries involved in planning for winter maintenance/new equipment installations.

## FishCounts
Adult fish counting ended on 10/31/2012 | PIT tag detections ended on 11/29/12
One fish two fish red fish blue fish
Black fish blue fish old fish new fish
Some are red and some are blue. some are old and some are new.
Some are sad and some are glad. And some are very, very bad.
Why are they sad and glad and bad? I dont know. Go ask your dad.
Some are thin and some are fat. The fat one has a yellow hat.
From there to here, from here to there, funny things everywhere.
Here are some who like to run. They run for fun in the hot, hot sun
Oh me! Oh my!
Oh me! Oh my!
What alot of funny things go by.
Some have two feet and some have four.
Some have six feet and some have more.
Where do they come from?
I cant say.
But I bet they have come a long, long way.
We see them come.
We see them go.
Some are fast.
And some are slow.
Some are high.
And some are low
Not one of them is like another.
Don't as us why.
Go ask your mother.

## TEMPS
JDA Fishway Temperatures
| min | max | avg
N ladder entrance
N ladder exit
S ladder entrance
S ladder exit

## Birds
SW T2: no birds
SW T3: SW T4
SW T1:
.
PH FB:
PH T1:
PH T2:
PH3: PH T4:
SW FB:

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 50 |  | 5
Mon | 49 |  | 5
Tues | 50 |  | 5
Wed | 50 |  | 4.5
Thur | 48 |  | 5
Fri | 48 |  | 5
Sat | 49 |  | 4
AVG: | 49.1429 | AVG: | 4.7857 | AVG | #DIV/0!
|  |  |  | MAX | #DIV/0!
|  |  |  | MIN | #DIV/0!
| NE1 | NE2 | S.Ent | SE1 | N.Ent | JBS Diff | Bay1 | Bay19
Sun | 8.1 | 8.1 | 1.2 | 10.1 | OOS | 4.6 | 1.6 | 1.2
Sun |  |  |  |  | OOS
Mon | 8.1 | 8.1 | 1.3 | 9.6 | OOS | 4.6 | 1.9 | 1.4
Mon |  |  |  |  | OOS
Tues | 8.1 | 8.1 | 1.3 | 9.6 | OOS | 4.6 | 2 | 1.6
Tues |  |  |  |  | OOS
Wed | 8.1 | 8 | 1.2 | 9.8 | OOS | 4.4 | 1.7 | 1.2
Wed |  |  |  |  | OOS
Thur | 8 | 8 | 1.3 | 9 | OOS | 4.8 | 1.8 | 1.2
Thur |  |  |  |  | OOS
Fri | 8.1 | 8.1 | 1.4 | 8.9 | OOS | 4.6 | 1.9 | 1.3
Fri |  |  |  |  | OOS
Sat | 8 | 8 | 1.1 | 9.7 | OOS | 4.7 | 1.6 | 1.4
Sat |  |  |  |  | OOS
AVG: | 8.0714 | 8.0571 | 1.2571 | 9.5286 | #DIV/0! | 4.6143 | 1.7857 | 1.3286