## SR
FISHWAY STATUS REPORT | [6 empty] | JOHN DAY DAM
Date: | 2011-12-31 | [7 empty] | JD/WC Project-Fisheries
Inspection Period: |  | 12/25 through 12/31/2011 | [6 empty] | P.O. Box 564
Rufus, OR 97050
Phone: 541-506-3800
Fishway inspections twice daily.
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 7 | Temperature: |  | 42 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 6 | Ft.
NORTH FISHWAY |  |  |  |  | OOS and dewatered since 7 November. ETR mid March 2012.
Exit differential |  |  | N/A | ≤ 0.5'
Exit Control weirs |  |  | N/A | Per forebay
Count station differential |  |  | N/A | ≤ 0.3'
Weir crest depth |  |  | N/A | 1.0' ± 0.1'
Entrance differential |  |  | N/A | 1.0' - 2.0' | AVG | #DIV/0!
Entrance weir EW1 |  |  | N/A | depth (≥ 8') | AVG | #DIV/0!
Entrance weir EW2 |  |  | N/A | No criteria
SOUTH FISHWAY |  |  |  |  | 2 AWS turbine operation; turbine 3 overhaul continues with ETR January 2012
Exit differential |  |  | 0 | ≤ 0.5'
Exit Control weirs |  |  | 0 | Per forebay | Set for MID forebay
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.2714
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | AVG | 8.7571
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | AVG
Bay 1 differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.6286
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0' | AVG | 1.3
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | AVG | 8.2286
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | AVG | 8.3571
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | AVG | 4.5857
Submersible traveling screens |  |  | 0 | visual inspect | All STSs are in the process of being removed for winter maintenance.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | No discrepancies.
Vert barrier screen drawdown |  |  | 0 | <1.5', wkly | No discrepancies
Spill volume |  |  | None | per FPP
Spill pattern |  |  | N/A | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: OOS for winter maintenance. ETR 1 April 2012
Maintenance: All flushing water pipes/valves were dewatered and SMF fully winterized by 11/18 PM.
Research: None
OTHER ISSUES:
Birds: see bird tab.
JD tailrace BRZ Avian Lines repair and improvements' contract is ongoing. All 125 lines will be available/properly tensioned for the 2012 juvenile passage
season starting on 1 April. JD Engineering and Fisheries are involved in coordination as needed.
Operations:
JD North fishway continues dewatered/OOS since 11/7. ETR is mid March 2012.
JD South fishway remains in regular service and is meeting all FPP criteria; it is scheduled for dewatering on 1/23/2012.
New construction:
JD North entrance improvements, 2-years' contract by Slayden Group is underway. The first year's construction activities are to be completed by mid
March 2012.
JD South AWS turbine 3 rehab continues on schedule. ETR is January, 2012. JD Maintenance is providing the contractor's support.
Maintenance:
JD JBS/ STS season ended on 12/15; JDS started removing STSs for winter maintenance on 12/19. All STS s will be reinstalled by 1 April, 2012.
JD South Fishway Automation is in service.
Gatewell drawdown: Conducted. All VBSs OK. All MU trashracks are raked as soon as their differential reaches 1.3' or higher.
Calibration: | 12/17/2011 All PLCs were accurate with a reading error of less than 0.3 '.
Research:
JD Fisheries team continues planning/ coordination of the 2012 research activities scheduled to take place at JD the next year.

## FishCounts
Fish counts ended Oct. 31, 2011. To resume in the spring 2012.

## Birds
S2:no birds observed
S1: no birds observed
S3: 1 cormorant
1 grebe
P4: 1 gull
1 cormorant
P3: 28 cormorants 4 gulls,
P2: no birds observed
P1: no birds observed
S4: 39 gulls on wing wall 3 cormorants
1 grebe

## AVGS
John Day:
| Temp: |  | Secchi: |  | Fallbacks
Sun | 42 |  | 6 |  | 0
Mon | 42 |  | 6 |  | 0
Tues | 42 |  | 6 |  | 0
Wed | 42 |  | 6 |  | 0
Thur | 42 |  | 6 |  | 0
Fri | 42 |  | 6 |  | 0
Sat | 42 | 8.3 | 6 |  | 0
AVG: | 42 | AVG: | 6 | AVG | 0
|  |  |  | MAX | 0
|  |  |  | MIN | 0
| NE1 | NE2 | S.Ent | SE1 | N.Ent | EW1 | JBS Diff | Bay1 | Bay19
Sun | 8.3 | 8.4 | 1.1 | 8.7 | oos | oos | 4.6 | 1.5 | 1.1
Sun |  |  |  |  | oos | oos
Mon | 8.1 | 8 | 1.2 | 8.6 | oos | oos | 4.7 | 1.5 | 1.2
Mon |  |  |  |  | oos | oos
Tues | 8.1 | 8.3 | 1 | 8.7 | oos | oos | 4.6 | 1.5 | 1.4
Tues |  |  |  |  | oos | oos
Wed | 8.3 | 8.6 | 1.3 | 9.1 | oos | oos | 4.6 | 1.5 | 1.1
Wed |  |  |  |  | oos | oos
Thur | 8.3 | 8.4 | 1.4 | 8.9 | oos | oos | 4.5 | 1.8 | 1.6
Thur |  |  |  |  | oos | oos
Fri | 8 | 8.2 | 1.4 | 8.6 | oos | oos | 4.6 | 1.8 | 1.6
Fri |  |  |  |  | oos | oos
Sat | 8.5 | 8.6 | 1.5 | 8.7 | oos | oos | 4.5 | 1.8 | 1.1
Sat |  |  |  |  | oos | oos
AVG: | 8.2286 | 8.3571 | 1.2714 | 8.7571 | #DIV/0! | #DIV/0! | 4.5857 | 1.6286 | 1.3