## SR
FISHWAY STATUS REPORT | [5 empty] | THE DALLES/JOHN DAY DAM
Date: 1/14/08 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 13/30/07-01/12/08 | [5 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.298.7406
Fishway inspections twice daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: | 14 | Temperature: |  | 40.8571 | F
|  |  | Out of Criteria | Limit | Comments |  | Secchi: | 5.8571 | Ft.
NORTH FISHWAY |  |  |  |  | Planned dewatering on 2/12/08.
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8') | Set at 9.5' depth
Entrance weir N2 |  |  |  | Closed | Bulkhead installed
PUD Intake differential |  |  | 0 | ≤ 0.5'
EAST FISHWAY |  |  |  |  | Dewatered since 12/5/07. Returns to service approx. 2/7/08.
Exit differential |  |  |  | ≤ 0.5'
Removable weirs 154-157 |  |  |  | Per forebay
Weir 158-159 differential |  |  |  | 1.0' ± 0.1'
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Junction pool weir JP6 |  |  |  | depth (≥ 7')
East entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir E1 |  |  |  | No criteria
Entrance weir E2 |  |  |  | depth (≥ 8')
Entrance weir E3 |  |  |  | depth (≥ 8')
Collection channel velocity |  |  |  | 1.5 - 4 fps
West entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir W1 |  |  |  | depth (≥ 8')
Entrance weir W2 |  |  |  | depth (≥ 8')
Entrance weir W3 |  |  |  | No criteria
South entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir S1 |  |  |  | depth (≥ 8')
Entrance weir S2 |  |  |  | depth (≥ 8')
JUVENILE PASSAGE
Sluicegate operation |  |  |  | units 1,5,18
Turbine trashrack drawdown |  |  |  | <1.5', wkly
Spill volume |  |  |  | 40%, 24hr
Spill Pattern |  |  |  | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: | 14 | Temperature: |  | 40.9286 | F
|  |  | Out of Criteria | Limit | Comments |  | Secchi: | 6 | Ft.
NORTH FISHWAY |  |  |  |  | Planned dewatering on 2/19/08.
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir EW1 |  |  | 0 | depth (≥ 8')
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY |  |  |  |  | Dewatered since 12/4/07. Returns to service approx. 2/14/08.
Exit differential |  |  |  | ≤ 0.5'
Hydraulic weir positions |  |  |  | Per forebay
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
South entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir SE1 |  |  |  | depth (≥ 8')
Collection channel velocity |  |  |  | 1.5 - 4 fps
Bay 1 differential |  |  |  | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  |  | 1.0' - 2.0'
Entrance weir NE1 |  |  |  | depth (≥ 8')
Entrance weir NE2 |  |  |  | depth (≥ 8')
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | MU 14 and 15 STSs remian in operation for the Battelle's optimization test.
Submersible traveling screens |  |  | 0 | visual inspect
Turbine trashrack drawdown |  |  |  | <1.5', wkly
Vert barrier screen drawdown
Spill volume |  |  |  | 30%, 24hr
Spill pattern |  |  |  | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | Dewatered since 15 September '07, will return to service on 1 April '08.
Maintenance:
Regular PM and equipment repairs underway in preparation for 2008 passage season.
A backup PDS water level sensor was proposed as an improvement to the SCADA system; procured and will be installed soon.
Thanks to Ed Harper , electrical foreman for this great idea!
OTHER ISSUES:
THE DALLES
Birds: Small numbers of cormorants, gulls and eagles around the project
Maintenance:
East fishway PMs and repairs continue; the main activities involve all entrance weirs, control section regulating weirs, and diffuser valves hardware.
Expansion joints repairs are being contracted out; anticipated to be performed in early February.
FU 2 runner blade's inspection revealed a large crack; project maintenance and HDC are investigating how it is to be repaired.
The past repairs of the blade's cracks were successful so there is no reason to doubt their effectiveness this time either.
Research:
U of I continues downloading their adult radiotelemetry receivers once a week.
Planning for the USGS equipment removal underway.
JOHN DAY
Birds: Small numbers of grebes and gulls in the forebay.
Maintenance:
South fishway PMs and repairs continue; fish turbine 3 overhaul is proceeding as scheduled: turbine disassembled, gearbox removed.
Fisheries presented a proposal at FPOM on 1/10 for the two turbine operation during the upcoming season; Mr. Clugston is to provide fish passage
data to select either 6.0 ' NE 1&2 weirs' depth (criteria is 8.0') or close two out of four floating orifices if necessary due to periods of low tailrace.
Expansion joints repairs are being contracted out; anticipated to be performed in early February.
Research:
U of I continues downloading their adult radiotelemetry receivers once a week.
Battelle was installing hydroacustic transducers and hydrophones at MU 14 & 15 and at spillbays 17&18 in preparation for the optimization test
to be performed during the week of 14 January.
Approved by;
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: | 42 | Secchi: | 6 | Velocity: |  | Temp: | 42 | Secchi: | 6 | Velocity:
| 42 |  | 6 |  |  |  | 42 |  | 6
| 41 |  | 6 |  | D |  | 41 |  | 6 |  | D
| 41 |  | 6 |  | E |  | 41 |  | 6 |  | E
| 41 |  | 6 |  | W |  | 41 |  | 6 |  | W
| 41 |  | 6 |  | A |  | 41 |  | 6 |  | A
| 41 |  | 6 |  | T |  | 41 |  | 6 |  | T
| 40 |  | 6 |  | E |  | 40 |  | 6 |  | E
| 41 |  | 6 |  | R |  | 40 |  | 6 |  | R
| 41 |  | 6 |  | E |  | 41 |  | 6 |  | E
| 41 |  | 6 |  | D |  | 40 |  | 6 |  | D
| 41 |  | 6 |  |  |  | 41 |  | 6
| 41 |  | 6 |  |  |  | 41 |  | 6
| 41 |  | 4 |  |  |  | 41 |  | 6
AVG: | 40.8571 | AVG: | 5.8571 |  |  | AVG: | 40.9286 | AVG: | 6