## SR
FISHWAY STATUS REPORT | [6 empty] | THE DALLES/JOHN DAY DAM
Date: | 2008-03-09 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 03/02 - 03/08/2008 | [6 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Note; AVGS tab contains detailed velocity, water temperature and water clarity data. | [8 empty] | Phone: 541.298.7406
Fishway inspections twice daily
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 41 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.5714 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8')
Entrance weir N2 |  |  | na | Closed
PUD Intake differential |  |  | 0 | ≤ 0.5'
EAST FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 0 | Per forebay | Auto adjusts at 1' increments - Weir 157 malfunction 2/16 - TR requested
Weir 158-159 differential |  |  | 0 | 1.0' ± 0.1'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Junction pool weir JP6 |  |  | 0 | depth (≥ 7') | Manually adjusted as needed.
East entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  |  | 0 | No criteria | Set at 3' depth due to low tailwater
Entrance weir E2 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Entrance weir E3 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.2528 | average in fps. | Performed by float test
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W2 |  |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W3 |  |  | 0 | No criteria | Manually adjusted as needed
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  |  | 0 | depth (≥ 8') | Set at 9' depth
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Set at 9' depth
JUVENILE PASSAGE
Sluicegate operation |  |  | 0 | units 1,5,18 | Sluicegates closed. Endgate open for orifice flow. Excessive sluicegate leakage.
Turbine trashrack drawdown |  |  | na | <1.5', wkly | Resumes Apr 1
Spill volume |  |  | na |  | closed
Spill Pattern |  |  | na | per FPP | closed
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 41.2857 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.8571 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir EW1 |  |  | 0 | depth (≥ 8')
Entrance weir EW2 |  |  | na | No criteria | Weir closed
SOUTH FISHWAY |  |  |  |  | on "Orifice Flow" 02/16
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  |  | 1 | depth (≥ 8') | 7.8'
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.5407 | average in fps. | Performed by float test
Bay 1 differential |  |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  |  | 0 | depth (≥ 8')
Entrance weir NE2 |  |  | 0 | depth (≥ 8')
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | visual inspect | Installed early on units 1-11. Remainder last week of Mar.
Turbine trashrack drawdown |  |  | na | <1.5', wkly | Resumes Apr 1
Vert barrier screen drawdown |  |  | na |  | Resumes Apr 1
Spill volume |  |  | na |  | Closed
Spill pattern |  |  | na | per FPP | Closed
Turbine Unit Priority |  |  | 6 | per FPP | Unit 1 out of service
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | Return to service Apr 1. Determining feasibility of season operation extension into Nov.
Maintenance:
Preventative maintenance in progress.
Backup Primary Dewatering Screen water level sensor to be installed.
Switch gate seal will not be modified for leakage concerns. Operational flushing will be provided to back side of gate to assure no fish stranding.
OTHER ISSUES:
THE DALLES
Overall bird numbers continue low.
USDA avian line modification logistics planned for last week of Mar. Cannot add spillway lines due to inability to close bridge traffic. Remaining
lines will be moved for better coverage. Hazing to start Apr 1.
Sluiceway chaingate excessive leakage. Coordination with FPOM resulted in keeping endgate open through March. Sluicegate flow resumes Apr 1.
Calibration: East entrance weir E3 out of tolerance limit. Maintenance notified. Depth remains within criteria.
Research:
U of I continues downloading their adult radiotelemetry receivers weekly.
USGS cleanup of equipment for previous years near completion.
JOHN DAY
Overall bird numbers continue low.
USDA avian line addition logistics planned for last week of Mar. Lines will be added to spillway. Hazing to start Apr 1.
Calibration: All entrance weirs and staff gages within tolerance limits.
Research:
U of I continues downloading their adult radiotelemetry receivers weekly.
Top spillway wier installation prep moved from spillbays 18/19 to 15/16.
Diving planned for Mar 10 (unit 14/15 tranducer removal) and Mar 11 (old release pipe removal from 3 spillbays)
approved by;
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## AVGS
|  | The Dalles | [6 empty] | John Day
[6 empty] | BAY | [6 empty] | Bay(s)
Temp: | 40 | Secchi: | 6 | Velocity: | 2.6303 | 1 | Temp: | 41 | Secchi: | 6 | Velocity: | 2.2785 | 2 - 4
| 41 |  | 6 |  | 2.4111 | 2 |  | 42 |  | 6 |  | 1.978 | 4 - 6
| 41 |  | 6 |  | 1.736 | 3 |  | 41 |  | 6 |  | 2.069 | 6 - 8
| 41 |  | 6 |  | 2.6303 | 4 |  | 41 |  | 6 |  | 1.8557 | 8 - 10
| 41 |  | 5 |  | 2.3459 | 5 |  | 41 |  | 6 |  | 2.8571 | 10 - 12
| 41 |  | 5.5 |  | 2.4111 | 6 |  | 42 |  | 5.5 |  | 3.0508 | 12 - 14
| 42 |  | 4.5 |  | 2.0667 | 7 |  | 41 |  | 5.5 |  | 2.9032 | 14 - 16
[5 empty] | 2.48 | 8 | [5 empty] | 3.3333 | 16 - 18
[5 empty] | 1.887 | SS |  |  |  |  | AVG: | 2.5407
[5 empty] | 1.736 | 9
[5 empty] | 2.2256 | 10
[5 empty] | 2.17 | 11
[5 empty] | 2.6303 | 12
[5 empty] | 1.8468 | 13
AVG: | 41 | AVG: | 5.5714 |  | 1.887 | 14 | AVG: | 41.2857 | AVG: | 5.8571
[5 empty] | 2.48 | 15
[5 empty] | 2.48 | 16
[5 empty] | 2.4111 | 17
[5 empty] | 2.48 | 18
[5 empty] | 2.1171 | 19
[5 empty] | 2.0186 | 20
[5 empty] | 2.48 | 21
|  |  |  | AVG: | 2.2528