## SR
FISHWAY STATUS REPORT | [6 empty] | THE DALLES/JOHN DAY DAM
Date: | 2007-04-29 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 04/22 - 04/28/2007 | [6 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.296.7406
Fishway inspections twice daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 50.5385 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 4.8077 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8')
Entrance weir N2 |  |  |  | Closed | Closed with bulkhead
PUD Intake differential |  |  | 0 | ≤ 0.5'
EAST FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 0 | per forebay
Weir 158-159 differential |  |  | 0 | 1.0' ± 0.1'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 1 | 1.0' ± 0.1' | 0.8' due to rapid forebay change, control PLC was responding properly.
Junction pool weir JP6 |  |  | 0 | depth (≥ 7') | Manually adjusted as needed >7' below tailwater
East entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  |  | 0 | closed | Manually adjusted as needed for optimal differential. Approx 6' depth.
Entrance weir E2 |  |  | 0 | depth (≥ 8')
Entrance weir E3 |  |  | 0 | depth (≥ 8')
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.6692 | fps at turbine bay 19 . | Float test avg 2.2fps from bay 21 to 13 on 4/17. | t avg 2.3 | from bay 21 to 13 4/24
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 0 | depth (≥ 8')
Entrance weir W2 |  |  | 0 | depth (≥ 8')
Entrance weir W3 |  |  | 0 |  | Manually adjusted as needed
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  |  | 14 | depth (≥ 8') | closed to achieve south entrance criteria differential during S2 weir repair
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Weir removed. Approx 16' entrance depth to channel floor. Repair underway.
ICE/TRASH SLUICEWAY
Sluice gate operation |  |  | 0 | 1, 5, 18 | 1-1/1-2/1-3, 5-2/5-3, 18-2/18-3 and Endgate full open.
SPILLWAY |  |  |  |  | 40% -24hr/day
Pattern |  |  | 0 | per FPP
UnitPriority |  |  | 0 | per FPP
1% Efficiency of turbines |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 50.5 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 4.9167 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | forebay 263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
Entrance differential |  |  | 0 | 1.0' - 2.0' | 3 of 6 pumps in operation. 1 pump out of service.
Entrance weir EW1 |  |  | 2 | depth (≥ 8') | 7.7 and 7.9' on 4/24. PLC was adjusted and its is working well.
Entrance weir EW2 |  |  |  | Closed | Closed with weir.
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  |  | 1 | depth (≥ 8') | 7.8' on 4/24. Routine setting adjustment was done and it worked well afterwards.
Collection channel velocity |  |  | 12 | 1.5 - 4 fps | 1.3 fps
Bay 1 differential |  |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  |  | 0 | depth (≥ 8')
Entrance weir NE2 |  |  | 0 | depth (≥ 8')
JUVENILE BYPASS SYSTEM
Forebay/conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | inspected
Gatewell drawdown |  |  | 0 | < 1.5' - wkly | No debris indication on intake trashracks or vertical barrier screens.
SPILLWAY |  |  |  |  | 0% day - 60% night
Pattern |  |  | 0 | per FPP
Unit Priority |  |  | 0 | per FPP
1% Efficiency of turbines |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | There were 6 screen cleaner #2 alarms. Cleaned manually as needed.
Maintenance: Trouble report was written for screen cleaner 2.
Light to Moderate debris at FDS, mostly tumbleweeds.
Full flow PIT installation complete and in operation. Construction site cleanup underway.
OTHER ISSUES:
THE DALLES
Avian predation:
Gulls first showed up and started feeding in the vicinity of The Dalles bridge approximately on 23/24 April. | [7 empty] | At the end of week about 30 gulls were
observed there. USDA avian hazing activities to commence on 1 May. USDA pikeminnow dam angling to start 14 May.
Maintenance:
Cannot close 5-2 sluice gate at unit 5 per Fish Passage Plan due to contractor work in that vicinity limiting crane space. Will close when clear.
Unit 18 scheduled to be out of service for overhaul maintenance May 21-Jul 13. 18-2, 18-3 sluicegates to be closed. 19-1 and 19-2 will be opened
during that time.
Units 5 and 6 out of service for maintenance.
South entrance S2 weir remains out for repair. Maintenance near complete installing new wheels. Target installation May 1.
Research:
Battelle DIDSON study planned to deploy their equipment on 4/28 but delayed to the next week due to cable failure.
Uof I adult radiotelemetry crew is downloading their antennas' receivers weekly. Also monitoring PIT tagged lamprey with their half-duplex system.
JOHN DAY
Avian predation:
Gulls first showed up and started feeding in the spillway tailrace/ SMF outfall on 23/24 April. At the end of week about 20 gulls were observed there.
Up to 35 grebes were observed in the forebay. USDA avian hazing activities to commence on 1 May. USDA pikeminnow angling to start 14 May.
Maintenance:
Spillbay # 3 was finally fixed and returned back to service on 4/25.
VBSs' top panel attachments found to be weak with rusted bolts at MU 12 which is likely the case in all units. Maintenance crew preparing a
plan to redesign/fix all top VBS top panel attachments at all units; meeting scheduled for 4/30.
Units 5-8 OOS due to line 2 maintenance outage. Expected return back to service on 4/30.
Research:
Uof I adult radiotelemetry crew is downloading their antennas' receivers weekly. Also monitoring PIT tagged lamprey with their half-duplex system.
Approved by;
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: |  | Secchi: | 4.5 | Velocity: | 2.6 | Temp: | 52 | Secchi: | 5 | Velocity: | 1.5
| 52 |  | 5 |  | 3 |  | 51 |  | 5 |  | 1.4
| 52 |  | 5 |  | 2.2 |  | 51 |  | 5 |  | 1.4
| 51 |  | 5 |  | 2.3 |  | 50 |  | 5 |  | 1.3
| 51 |  | 5 |  | 2.3 |  | 49 |  | 5 |  | 1.3
| 50 |  | 5 |  | 2.2 |  | 50 |  | 4.5 |  | 1.2
| 50 |  | 5 |  | 2.6 | [5 empty] | 1.3
| 50 |  | 5 |  | 2.3 | [5 empty] | 1.3
| 50 |  | 5 |  | 1.8 | [5 empty] | 1.3
| 51 |  | 5 |  | 3.2 | [5 empty] | 1.1
| 50 |  | 4.5 |  | 3.4 | [5 empty] | 1.5
| 50 |  | 4.5 |  | 3.4
| 50 |  | 4 |  | 3.4
50
AVG: | 50.5385 | AVG: | 4.8077 | AVG: | 2.6692 | AVG: | 50.5 | AVG: | 4.9167 | AVG: | 1.3273