## SR
FISHWAY STATUS REPORT | [7 empty] | THE DALLES/JOHN DAY DAM
Date: | 2008-05-26 | [8 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 5/18/2008 - 5/24/2008 | [7 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.298.7406
Fishway inspections twice daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 56.4286 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 3.4286 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8') | Set at 9.5' depth
Entrance weir N2 |  |  |  | Closed | Bulkhead installed
PUD Intake differential |  |  | 0 | ≤ 0.5' | PUD trashrack raked 5/20.
EAST FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 0 | Per forebay | Auto adjusts at 1' increments
Weir 158-159 differential |  |  | 1 | 1.0' ± 0.1' | Weir 158 differential 0.4'. Malfunction due to very low forebay and manually adjusted.
Count station differential |  |  | 0 | ≤ 0.3' | Count station down stream picket leads raked of aquatic weeds 5/23 and 5/24.
Weir crest depth |  |  | 1 | 1.0' ± 0.1' | 1.6', weir 158 malfunction due to very low forebay. Manually adjusted.
Junction pool weir JP6 |  |  | 0 | depth (≥ 7') | Manually adjusted as needed.
East entrance differential |  |  | 2 | 1.0' - 2.0' | 0.6', 0.9', PLC malfunction due to high tailwater; electricians fixed.
Entrance weir E1 |  |  | 0 | No criteria | Manually adjusted as needed for criteria differential
Entrance weir E2 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Entrance weir E3 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.305 | average in fps. |  | See tab below for more complete velocities.
Transportation channel velocity |  |  | 0 | 1.5 - 4 fps | 2.3 | average in fps.
North entrance velocity |  |  | 0 | 1.5 - 4 fps | 2.2 | average in fps.
South rock channel velocity |  |  | 0 | 1.5 - 4 fps | 2.8 | average in fps.
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W2 |  |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W3 |  |  | 0 | No criteria | Manually adjusted as needed
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  |  | 0 | depth (≥ 8') | Set at 9' depth
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Set at 9' depth
JUVENILE PASSAGE
Sluicegate operation |  |  | 0 | units 1,5,18 | Unit 7 sluicegate operation due to MU5 outage for intermediate oil shaft leak.
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | Range: 0.2' - 0.8'.
Spill volume |  |  | 2 | 40%, 24hr | 43%, 41.8%. |  | Due to high flows.
Spill Pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 56.1429 | F
|  |  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 4.3714 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir EW1 |  |  | 0 | depth (≥ 8')
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  |  | 0 | depth (≥ 8')
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.6126 | average in fps. |  | See tab below for more complete velocities.
South entrance velocity |  |  | 1 | 1.5 - 4 fps | 5.4 | average in fps.
North entrance velocity |  |  | 0 | 1.5 - 4 fps | 2.1 | average in fps.
Bay 1 differential |  |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  |  | 0 | depth (≥ 8')
Entrance weir NE2 |  |  | 0 | depth (≥ 8')
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | visual inspect | Monthly inspection schedule
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly | Range: 0.3' - 0.9'.
Vert barrier screen drawdown |  |  | 0 |  | Range: 0.3' - 0.8'.
Spill volume |  |  | 0 | 30/40% | 24 hrs spill alternating between 30 and 40 % according to study design
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | In service through mid November.
Maintenance: There were no maintenance issues for the reporting period.
There were 1,699 total strikes on the counter at the FDS (average/high/low - 243/607/103).
Debris at FDS: Debris was moderate to high at the separator and consisted mostly of sticks, aquatic weeds, and plastic.
Research: Battelle/PSMFC crew continue their daily collection and tagging juvenile salmonids, seven days a week.
Approximately 895 yearling Chinook smolt and 895 steelhead smolt were collected for Battelle researchers.
OTHER ISSUES:
THE DALLES
Birds: A maximum of 250 gulls observed feeding near the bridge. USDA are currently hazing the gulls.
Maintenance:
A few minor PLC/control problems have occurred at the east ladder exit and entrance due to abnormally large forebay/ tailrace levels fluctuations.
Manual operation is required during the periods of high TW.
West sluice gate 7-1 open due to main unit #5 forced outage for intermediate oil shaft leak extended to 6/2.
Calibration: Completed on 5/22; all within criteria except north entrance weir N1 which was out of criteria by 0.1'. Gatewell drawdown completed
5/24; all within criteria.
Research: The design for the spill wall between bays 8 and 9 is in the final stage of preparation for the May '08 contract advertisement.
University of Idaho adult lamprey crew video monitoring of passage at night has begun; adult radiotelemetry crew are currently downloading
receivers weekly.
JOHN DAY
Birds: A maximum of 400 gulls have been observed feeding in the spillway tailrace. USDA continues with hazing the gulls; funding for long range
rockets have been approved and are waiting their delivery. A maximum of 100 grebes and 40 gulls observed in the powerhouse forebay.
A new fishing platform has been built downstream of the powerhouse on the Oregon side of the river. CRITFC enforcement is aware that it is within
200' of the east fishway entrance.
of the fishway entrance.
Maintenance: The south fish turbine #3 overhaul continues and is proceeding as scheduled for RTS in March '09.
The north fish pump #3 repair is almost complete, mechanics are putting it together, and RTS next week.
North fish pump # 4 assembly was completed. However, there were some metal shavings found after a test run so mechanics continue working to
identify this problem.
Calibration: Calibrations were completed on 5/23; all within criteria. Gatewell drawdown was completed 5/24; all within criteria.
Research: USGS drogue releases from the spillwall and SMF outfall and will continue with 10 drogues a couple times per week for the duration
of TSW evaluations.
Battelle powerhouse and spillway acoustics study will continue 24/7 through early June for the spring migrants component of TSW evaluation.
University of Idaho adult radiotelemetry crew are downloading their ladder receivers weekly.
approved by;
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## FishCounts
THE DALLES 2008
| East | North | East | North | East | North | East | Norh
| ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd | Shad | Shad
2008-05-08 | 1730 | 132 | 306 | 5 | 18 | 0 | 5 | 0
2008-05-09 | 1902 | 13 | 368 | 0 | 5 | 0 | 12 | 0
2008-05-10 | 2197 | 8 | 366 | 0 | 7 | 0 | 0 | 0
2008-05-11 | 2560 | 599 | 473 | 25 | 8 | 1 | 0 | 0
2008-05-12 | 1800 | 73 | 689 | 6 | 6 | 0 | 0 | 0
2008-05-13 | 2414 | 17 | 685 | 1 | 13 | 0 | 14 | 0
2008-05-14 | 3815 | 331 | 1380 | 5 | 8 | 0 | 6 | 0
2008-05-15
2008-05-16
2008-05-17
JOHN DAY 2008
| South | North | South | North | South | North | South | North | South | North
| ChinAdult | ChinAdult | ChinJack | ChinJack | Sthd | Sthd | Sockeye | Sockeye | Lamprey | Lamprey
2008-05-08 | 1694 | 794 | 179 | 137 | 12 | 15
2008-05-09 | 1090 | 570 | 162 | 121 | 6 | 7
2008-05-10 | 1111 | 895 | 157 | 200 | 9 | 8
2008-05-11 | 1237 | 895 | 275 | 151 | 2 | 15
2008-05-12 | 1723 | 750 | 318 | 155 | 4 | 1
2008-05-13 | 956 | 713 | 252 | 202 | 2 | 69
2008-05-14 | 1021 | 781 | 199 | 202 | 16 | 14 |  |  | 1 | 0
2008-05-15 | 2078 | 1325 | 595 | 400 | 10 | 189 |  |  | 16 | 0
2008-05-16
2008-05-17

## TEMPS
Avg: | 54.75 | Avg: | 55.15
Min: | 52.28 | Min: | 52.2
Max: | 56.64 | Max: | 60
Avg: | 54.84 | Avg: | 54.73
Min: | 52.12 | Min: | 52.2
Max: | 56.81 | Max: | 56.64
Avg: | 55.12 | Avg: | 55.06
Min: | 52.34 | Min: | 52.34
Max: | 57.25 | Max: | 57.33

## Velocities
 | time axis 2008-04-12 to 2009-01-29
The Dalles Collection Channel
Bay(s) | Enter time |  | Seconds | Velocity (f/s)
Bay 1 | 0:14 | 854 | 33 | 2.6303 | 2008-04-26: 1.97; 2008-05-01: 2.2842; 2008-05-08: 3.3385; 2008-05-15: 2.2256; 2008-05-22: 2.6303
Bay 2 | 0:14 | 821 | 47 | 1.8468 | 2008-04-26: 2.12; 2008-05-01: 2.0186; 2008-05-08: 3.1; 2008-05-15: 2.8933; 2008-05-22: 1.8468
Bay 3 | 0:13 | 774 | 35 | 2.48 | 2008-04-26: 2.35; 2008-05-01: 2.48; 2008-05-08: 3.2148; 2008-05-15: 2.8; 2008-05-22: 2.48
Bay 4 | 0:12 | 739 | 40 | 2.17 | 2008-04-12: 2.23; 2008-04-26: 2.23; 2008-05-01: 2.5529; 2008-05-08: 2.8933; 2008-05-15: 2.9931; 2008-05-22: 2.17
Bay 5 | 0:12 | 699 | 33 | 2.6303 | 2008-04-12: 1.7; 2008-04-26: 2.07; 2008-05-01: 2.48; 2008-05-08: 2.7125; 2008-05-15: 2.6303; 2008-05-22: 2.6303
Bay 6 | 0:11 | 666 | 47 | 1.8468 | 2008-04-12: 1.67; 2008-04-26: 1.85; 2008-05-01: 2.17; 2008-05-08: 2.9931; 2008-05-15: 2.5529; 2008-05-22: 1.8468
Bay 7 | 0:10 | 619 | 34 | 2.5529 | 2008-04-12: 2.35; 2008-04-26: 2.17; 2008-05-01: 2.4111; 2008-05-08: 2.8933; 2008-05-15: 2.8933; 2008-05-22: 2.5529
Bay 8 | 0:10 | 585 | 37 | 2.3459 | 2008-04-12: 2.23; 2008-04-26: 2.17; 2008-05-01: 2.4111; 2008-05-08: 2.8; 2008-05-15: 2.8933; 2008-05-22: 2.3459
SS | 0:09 | 548 | 41 | 2.1171 | 2008-04-12: 1.7; 2008-04-26: 1.81; 2008-05-01: 2.0186; 2008-05-08: 2.9931; 2008-05-15: 2.7125; 2008-05-22: 2.1171
Bay 9 | 0:08 | 507 | 37 | 2.3459 | 2008-04-12: 1.74; 2008-04-26: 1.5; 2008-05-01: 1.7714; 2008-05-08: 1.8468; 2008-05-15: 2.5529; 2008-05-22: 2.3459
Bay 10 | 0:08 | 470 | 34 | 2.5529 | 2008-04-12: 2.07; 2008-04-26: 2.28; 2008-05-01: 2.1171; 2008-05-08: 2.3459; 2008-05-15: 2.9931; 2008-05-22: 2.5529
Bay 11 | 0:07 | 436 | 43 | 2.0186 | 2008-04-12: 1.93; 2008-04-26: 2.23; 2008-05-01: 2.3459; 2008-05-08: 2.4111; 2008-05-15: 2.5529; 2008-05-22: 2.0186
Bay 12 | 0:07 | 393 | 48 | 1.8083 | 2008-04-12: 1.67; 2008-04-26: 1.77; 2008-05-01: 2.2256; 2008-05-08: 2.9931; 2008-05-15: 2.48; 2008-05-22: 1.8083
Bay 13 | 0:06 | 345 | 42 | 2.0667 | 2008-04-12: 1.97; 2008-04-26: 1.89; 2008-05-01: 2.0667; 2008-05-08: 2.8; 2008-05-15: 1.9289; 2008-05-22: 2.0667
Bay 14 | 0:05 | 303 | 30 | 2.8933 | 2008-04-12: 1.89; 2008-04-26: 1.85; 2008-05-01: 2.3459; 2008-05-08: 2.2256; 2008-05-15: 2.6303; 2008-05-22: 2.8933
Bay 15 | 0:05 | 273 | 33 | 2.6303 | 2008-04-12: 1.86; 2008-04-26: 1.47; 2008-05-01: 2.3459; 2008-05-08: 2.8933; 2008-05-15: 2.48; 2008-05-22: 2.6303
Bay 16 | 0:04 | 240 | 46 | 1.887 | 2008-04-12: 1.58; 2008-04-26: 1.85; 2008-05-01: 1.736; 2008-05-08: 2.7125; 2008-05-15: 2.2842; 2008-05-22: 1.887
Bay 17 | 0:03 | 194 | 61 | 1.423 | 2008-04-12: 2.07; 2008-04-26: 2.07; 2008-05-01: 1.7714; 2008-05-08: 2.4111; 2008-05-15: 1.55; 2008-05-22: 1.423
Bay 18 | 0:02 | 133 | 31 | 2.8 | 2008-04-12: 2.28; 2008-04-26: 1.89; 2008-05-01: 2.1171; 2008-05-08: 2.6303; 2008-05-15: 2.5529; 2008-05-22: 2.8
Bay 19 | 0:02 | 102 | 33 | 2.6303 | 2008-04-12: 2.07; 2008-04-26: 2.02; 2008-05-01: 2.6303; 2008-05-08: 2.8; 2008-05-15: 2.6303; 2008-05-22: 2.6303
Bay 20 | 0:01 | 69 | 34 | 2.5529 | 2008-04-12: 1.77; 2008-04-26: 2.07; 2008-05-01: 2.4111; 2008-05-08: 2.8933; 2008-05-15: 3.1; 2008-05-22: 2.5529
Bay 21 | 0:01 | 35 | 35 | 2.48 | 2008-04-26: 1.89; 2008-05-01: 2.48; 2008-05-08: 2.8; 2008-05-15: 3.2148; 2008-05-22: 2.48
Average |  |  |  | 2.305 | 2008-04-12: 1.9322; 2008-04-26: 1.98; 2008-05-01: 2.236; 2008-05-08: 2.7592; 2008-05-15: 2.6157; 2008-05-22: 2.305
The Dalles Transportation Channel
Bay#'s | Enter time |  | Seconds | Velocity (f/s)
Bay 1 | 0:14 | 851 | 40 | 2.17 | 2008-04-12: 2.28; 2008-04-26: 2.12; 2008-05-01: 2.0186; 2008-05-08: 2.4111; 2008-05-15: 2.2256; 2008-05-22: 2.17
Bay 2 | 0:14 | 811 | 39 | 2.2256 | 2008-04-12: 1.89; 2008-04-26: 2.17; 2008-05-01: 2.1171; 2008-05-08: 1.8083; 2008-05-15: 2.2256; 2008-05-22: 2.2256
Bay 3 | 0:13 | 772 | 37 | 2.3459 | 2008-04-12: 1.97; 2008-04-26: 2.12; 2008-05-01: 2.2256; 2008-05-08: 1.736; 2008-05-15: 2.0667; 2008-05-22: 2.3459
Bay 4 | 0:12 | 735 | 38 | 2.2842 | 2008-04-12: 2.12; 2008-04-26: 2.07; 2008-05-01: 2.0667; 2008-05-08: 2.48; 2008-05-15: 2.0667; 2008-05-22: 2.2842
Bay 5 | 0:12 | 697 | 36 | 2.4111 | 2008-04-12: 2.17; 2008-04-26: 2.07; 2008-05-01: 2.0667; 2008-05-08: 2.48; 2008-05-15: 2.0186; 2008-05-22: 2.4111
Bay 6 | 0:11 | 661 | 38 | 2.2842 | 2008-04-12: 2.23; 2008-04-26: 2.07; 2008-05-01: 2.1171; 2008-05-08: 2.5529; 2008-05-15: 2.1171; 2008-05-22: 2.2842
Bay 7 | 0:10 | 623 | 39 | 2.2256 | 2008-04-12: 1.89; 2008-04-26: 1.85; 2008-05-01: 2.1171; 2008-05-08: 2.3459; 2008-05-15: 1.9727; 2008-05-22: 2.2256
Bay 8 | 0:10 | 584 | 38 | 2.2842 | 2008-04-12: 1.93; 2008-04-26: 2.17; 2008-05-01: 2.2256; 2008-05-08: 2.48; 2008-05-15: 2.2256; 2008-05-22: 2.2842
SS | 0:09 | 546 | 42 | 2.0667 | 2008-04-12: 2.02; 2008-04-26: 2.02; 2008-05-01: 2.0667; 2008-05-08: 2.17; 2008-05-15: 2.17; 2008-05-22: 2.0667
Bay 9 | 0:08 | 504 | 40 | 2.17 | 2008-04-12: 2.02; 2008-04-26: 2.12; 2008-05-01: 2.2256; 2008-05-08: 2.2842; 2008-05-15: 2.2842; 2008-05-22: 2.17
Bay 10 | 0:08 | 464 | 39 | 2.2256 | 2008-04-12: 2.02; 2008-04-26: 2.28; 2008-05-01: 2.0667; 2008-05-08: 2.17; 2008-05-15: 2.1171; 2008-05-22: 2.2256
Bay 11 | 0:07 | 425 | 44 | 1.9727 | 2008-04-12: 2.02; 2008-04-26: 2.23; 2008-05-01: 2.0667; 2008-05-08: 2.1171; 2008-05-15: 2.2842; 2008-05-22: 1.9727
Bay 12 | 0:06 | 381 | 37 | 2.3459 | 2008-04-12: 2.02; 2008-04-26: 2.17; 2008-05-01: 2.0186; 2008-05-08: 1.9727; 2008-05-15: 2.17; 2008-05-22: 2.3459
Bay 13 | 0:06 | 344 | 38 | 2.2842 | 2008-04-12: 2.12; 2008-04-26: 2.02; 2008-05-01: 1.887; 2008-05-08: 2.2256; 2008-05-15: 2.2256; 2008-05-22: 2.2842
Bay 14 | 0:05 | 306 | 38 | 2.2842 | 2008-04-12: 2.17; 2008-04-26: 2.12; 2008-05-01: 1.9727; 2008-05-08: 2.0186; 2008-05-15: 2.2256; 2008-05-22: 2.2842
Bay 15 | 0:04 | 268 | 37 | 2.3459 | 2008-04-12: 2.17; 2008-04-26: 1.97; 2008-05-01: 1.9289; 2008-05-08: 1.9289; 2008-05-15: 2.2842; 2008-05-22: 2.3459
Bay 16 | 0:04 | 231 | 38 | 2.2842 | 2008-04-12: 1.93; 2008-04-26: 1.89; 2008-05-01: 1.9289; 2008-05-08: 2.0667; 2008-05-15: 2.2256; 2008-05-22: 2.2842
Bay 17 | 0:03 | 193 | 38 | 2.2842 | 2008-04-12: 1.93; 2008-04-26: 2.07; 2008-05-01: 2.0186; 2008-05-08: 2.1171; 2008-05-15: 2.0667; 2008-05-22: 2.2842
Bay 18 | 0:03 | 155 | 39 | 2.2256 | 2008-04-12: 1.89; 2008-04-26: 1.89; 2008-05-01: 1.887; 2008-05-08: 1.9289; 2008-05-15: 1.887; 2008-05-22: 2.2256
Bay 19 | 0:02 | 116 | 38 | 2.2842 | 2008-04-12: 1.97; 2008-04-26: 1.85; 2008-05-01: 1.8468; 2008-05-08: 2.0186; 2008-05-15: 1.8468; 2008-05-22: 2.2842
Bay 20 | 0:01 | 78 | 41 | 2.1171 | 2008-04-12: 1.64; 2008-04-26: 1.74; 2008-05-01: 2.2256; 2008-05-08: 2.17; 2008-05-15: 2.0667; 2008-05-22: 2.1171
Bay 21 | 0:01 | 37 | 37 | 2.3459 | 2008-04-26: 1.74; 2008-05-01: 2.3459; 2008-05-08: 2.2256; 2008-05-15: 2.3459; 2008-05-22: 2.3459
Average |  |  |  | 2.2485 | 2008-04-12: 2.019; 2008-04-26: 2.03; 2008-05-01: 2.0655; 2008-05-08: 2.1686; 2008-05-15: 2.1417; 2008-05-22: 2.2485
The Dalles North entrance
d/s of PUD bridge to start of 180 bend
Distance | Enter time | Seconds |  | Velocity (f/s)
156' | 0:01 | 70 |  | 2.2286 | 2008-04-12: 2.74; 2008-04-26: 2.2; 2008-05-01: 2.6441; 2008-05-08: 1.81; 2008-05-15: 2.08; 2008-05-22: 2.2286
Tailwater
The Dalles South Rock Channel
d/s edge of sluice brdg. to u/s edge of Westrick brdg.
Distance | Enter time | Seconds |  | Velocity (f/s)
570' | 0:03 | 205 |  | 2.7805 | 2008-04-12: 3.02; 2008-04-26: 3.02; 2008-05-01: 2.9381; 2008-05-08: 3.08; 2008-05-15: 2.395; 2008-05-22: 2.7805
Tailwater
The Dalles South Rock Channel
d/s edge of sluice bridge to u/s edge of s. ent. deck
(cannot float lower half at high TW due to support)
Distance | Enter time | Seconds |  | Velocity (f/s)
1480' | 0:07 | 441 |  | 3.356 | 2008-04-12: 3.18; 2008-04-26: 3.36; 2008-05-01: N/A; 2008-05-08: N/A; 2008-05-15: N/A; 2008-05-22: N/A
Tailwater
John Day Collection Channel
| Enter time |  | Seconds | Velocity (f/s)
Bay 1&2 | 0:01 | 87 | 72 | 2.5 | 2008-04-26: 2.54; 2008-05-01: 2.4; 2008-05-08: 2.2785; 2008-05-15: 2.6471; 2008-05-22: 2.5
Bay 3&4 | 0:03 | 159 | 81 | 2.2222 | 2008-04-26: 2.65; 2008-05-01: 2.43; 2008-05-08: 2.5; 2008-05-15: 2.2785; 2008-05-22: 2.2222
Bay 5&6 | 0:04 | 240 | 77 | 2.3377 | 2008-04-26: 2.69; 2008-05-01: 2.25; 2008-05-08: 2.5714; 2008-05-15: 2.6087; 2008-05-22: 2.3377
Bay 7&8 | 0:05 | 317 | 103 | 1.7476 | 2008-04-26: 2.54; 2008-05-01: 2.02; 2008-05-08: 2.3377; 2008-05-15: 2.6087; 2008-05-22: 1.7476
Bay 9&10 | 0:07 | 420 | 47 | 3.8298 | 2008-04-26: 2.47; 2008-05-01: 2.69; 2008-05-08: 2.1951; 2008-05-15: 2.25; 2008-05-22: 3.8298
Bay 11&12 | 0:08 | 467 | 79 | 2.2785 | 2008-04-26: 2.4; 2008-05-01: 2.4; 2008-05-08: 2.6087; 2008-05-15: 2.2785; 2008-05-22: 2.2785
Bay 13&14 | 0:09 | 546 | 83 | 2.1687 | 2008-04-26: 2.34; 2008-05-01: 2; 2008-05-08: 2.4658; 2008-05-15: 2.5352; 2008-05-22: 2.1687
Bay 15&16 | 0:10 | 629 | 56 | 3.2143 | 2008-04-26: 3.67; 2008-05-01: 3.4; 2008-05-08: 3.4615; 2008-05-15: 3.3962; 2008-05-22: 3.2143
Bay 17&18 | 0:11 | 685 | 56 | 3.2143 | 2008-04-26: 3.67; 2008-05-01: 3.4; 2008-05-08: 3.4615; 2008-05-15: 3.3962; 2008-05-22: 3.2143
|  | Average |  | 2.6126 | 2008-04-26: 2.77; 2008-05-01: 2.55; 2008-05-08: 2.6534; 2008-05-15: 2.6666; 2008-05-22: 2.6126
John Day South Entrance
Distance | Enter time | Seconds |  | Velocity (f/s)
49' | 0:00 | 9 |  | 5.4444 | 2008-04-26: 4.08; 2008-05-01: 4.9; 2008-05-08: 3.7692; 2008-05-15: 4.4545; 2008-05-22: 5.4444
John Day North Entrance
Lowest weir to start of deck 180 curve
Distance | Enter Time | Seconds |  | Velocity ((f/s)
139' | 0:01 | 66 |  | 2.1061 | 2008-04-26: 2.44; 2008-05-01: 2.11; 2008-05-08: 2.4386; 2008-05-15: 2.3559; 2008-05-22: 2.1061
Comments
Note on E1: g2oddpsk: Highlight # column, edit, copy, click on cell where you want to copy it to, edit, paste special, values.
Note on K94: g2oddpsk: TD's East entrance channel - 89.8', TW 86.2', diff. 1.6' (stillwell readings, PLC not functiong as a result of high TW). Net head 71.4', river dischange 385 KCFS; FU's both on, 12.2 MW, 13,2 MW, Tot discharge 5510. Bay 17 CC, low velocity due to high TW and float hitting pipes in channel.

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: | 56 | Secchi: | 3.5 | Velocity: | 2.305 | Temp: | 56 | Secchi: | 4.5 | Velocity: | 2.6126
| 56 |  | 3.5 |  |  |  | 57 |  | 4
| 56 |  | 3.5 |  |  |  | 57 |  | 4.6
| 57 |  | 3.5 |  |  |  | 57 |  | 4.5
| 58 |  | 4 |  |  |  | 56 |  | 4.5
| 56 |  | 3 |  |  |  | 56 |  | 4.5
| 56 |  | 3 |  |  |  | 54 |  | 4
AVG: | 56.4286 | AVG: | 3.4286 | AVG: | 2.305 | AVG: | 56.1429 | AVG: | 4.3714 | AVG: | 2.6126