## SR
FISHWAY STATUS REPORT | [6 empty] | THE DALLES/JOHN DAY DAM
Date: 07/15/07 | [8 empty] | TD/JD/WC Project-Fisheries
Inspection Period: 07/08-07/14/2007 | [8 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.296.7406
Fishway inspections twice daily.
The Dalles Dam |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 68.2857 | F
|  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 4.6429 | Ft.
NORTH FISHWAY
Exit differential |  | 0 | ≤ 0.5'
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1' | Set at 1.0' for non-shad passage
Entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  | 0 | depth (≥ 8') | Set at 9.5' depth
Entrance weir N2 |  |  | Closed | Bulkhead installed
PUD Intake differential |  | 0 | ≤ 0.5'
EAST FISHWAY
Exit differential |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  | 0 | Per forebay | Auto adjusts at 1' increments
Weir 158-159 differential |  | 0 | 1.0' ± 0.1'
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1' | Set at 1.0' for non-shad passage
Junction pool weir JP6 |  | 0 | depth (≥ 7') | Manually adjusted as needed. |  |  | 6.7' low tailwater
East entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  | 0 | No criteria | Manually adjusted as needed for criteria differential
Entrance weir E2 |  | 0 | depth (≥ 8') | Set at 12.5' depth
Entrance weir E3 |  | 0 | depth (≥ 8') | Set at 12.5' depth
Collection channel velocity |  | 1 | 1.5 - 4 fps | 2.0385 | average in fps.
West entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W2 |  | 0 | depth (≥ 8') | Set at 10' depth
Entrance weir W3 |  | 0 | No criteria | Manually adjusted as needed
South entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  | 1 | depth (≥ 8') | Set at 9' depth
Entrance weir S2 |  | 1 | depth (≥ 8') | Set at 9' depth
ICE/TRASH SLUICEWAY
Sluice gate operation |  | 0 | units 1,5,18 | Sluicegates 1-1,1-2,1-3,5-2,19-2,19-3 and endgate open
SPILLWAY |  |  |  | 40%, 24hr/day
Pattern |  | 0 | per FPP
Turbine UnitPriority |  | 0 | per FPP
Turbine 1% Efficiency |  | 0 | per FPP
John Day Dam |  | Inspections | Criteria | Total Number of Inspections: |  |  | 14 | Temperature: |  | 68.8571 | F
|  | Out of Criteria | Limit | Comments |  |  |  | Secchi: | 4.7143 | Ft.
NORTH FISHWAY
Exit differential |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  | 0 | Per forebay | Set for forebay <263'
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1' | Set at 1.0' for non-shad passage
Entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir EW1 |  | 1 | depth (≥ 8') | Set at 9.5' |  | 7.2', 7.8' low tailwater |  |  | only 2 fish pumps running
Entrance weir EW2 |  | 0 | Weir closed
SOUTH FISHWAY
Exit differential |  | 0 | ≤ 0.5'
Hydraulic weir positions |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  | 0 | ≤ 0.3'
Weir crest depth |  | 0 | 1.0' ± 0.1' | Set at 1.0' for non-shad passage
South entrance differential |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  | 0 | depth (≥ 8') | Set at 9' |  | 7.9'
Collection channel velocity |  | 13 | 1.5 - 4 fps | 1.2154 | average in fps.
Bay 1 differential |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  | 0 | depth (≥ 8') | Set at 9.3' |  | 7.8' low tailwater
Entrance weir NE2 |  | 0 | depth (≥ 8') | Set at 9.3' |  | 7.9' low tailwater
JUVENILE BYPASS SYSTEM
Forebay/conduit differential |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  | 0 | visual inspect | Monthly inspection schedule
Gatewell drawdown |  | 0 | <1.5' - wkly | Range;
SPILLWAY |  |  |  | 0% day, 60% night
Pattern |  | 0 | per FPP
Turbine Unit Priority |  | 0 | per FPP | MU-2 and MU-4 not in use
Turbine 1% Efficiency |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: PDS screen cleaner out of service. Screens manually cleaned as needed.
| JBS conduit sensor out of service during periods of high temperature. |  |  |  |  | Troubleshooting, waiting for new parts to install.
New protocol developed to limit stress in passing smolts when the water temps are above 70 degrees F. Only condition sampling will continue
twice a week, with small target of 100 fish each time. An attempt to switch to full flow operations is also expected.
Maintenance: None
Debris at FDS: Light except for shad which are coming down in high numbers.
OTHER ISSUES:
THE DALLES
Moderate gull numbers over spillway tailrace. Majority juvnenile gulls. Highest concentration on bay 6 eddy line, under avian lines. USDA periodic
hazing with limited temporary effectiveness.
USDA pikeminnow dam angling underway with high catch rate of large pikeminnow. Primary areas are sluiceway outfall and powerhouse tailrace.
Entrance calibration checked 7/14. West entrance tailwater and channel off by 0.5'. Maintenance notified.
Oil change of east exit weir gearboxes planned for august. Optimal secaonday containment to be implimented.
Mid season ROV grating inspection scheduled for Aug 7. North fishway auxiliary water outage estimate 3 hours and east fishway 6 hours.
Research; U of I adult salmonids telemetry and half-duplex PIT lamprey monitoring continues with weekly data collection.
JOHN DAY
Moderate gull numbers over spillway tailrace. High gull and grebe numbers in forebay. Majority juvnenile gulls. USDA periodic hazing with limited
temporary effectiveness. Pelicans (10-15) observed on island downstream of dam.
USDA pikeminnow dam angling underway with high catch rate of large pikeminnow. Primary fishing areas are tailrace navlock wall and powerhouse.
Entrance calibration checked 7/14. Bay 19 Channel off by 0.5' so the staff gauge needs to be properly seated, Structural crew notified.
North entrance PLC automation problems relating to spillway turbulence. Maitenance working on solution. EW1 adjusted manually as needed.
Mid season ROV grating inspection scheduled for Aug 8. North fishway auxiliary water outage estimate 3 hours and south fishway 5 hours.
Research; U of I adult salmonids telemetry and half-duplex PIT lamprey monitoring continues with weekly data collection.

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: | 67 | Secchi: | 5 | Velocity: | 3 | Temp: | 67 | Secchi: | 5 | Velocity: | 1.1
| 67 |  | 5 |  |  |  | 67 |  | 5 |  | 1.3
| 69 |  | 5.5 |  | 2.7 |  | 69 |  | 5.5 |  | 1.3
| 67 |  | 5 |  | 2.2 |  | 69 |  | 5.5 |  | 1.4
| 69 |  | 5.5 |  | 1.3 |  | 70 |  | 5
| 69 |  | 3 |  | 1.5 |  | 71 |  | 3.5 |  | 1.3
| 70 |  | 3.5 |  | 1.9 |  | 69 |  | 3.5 |  | 1.1
[5 empty] | 1.5 | [5 empty] | 1.2
[5 empty] | 1.7 | [5 empty] | 1.2
[5 empty] | 2.1 | [5 empty] | 1.2
[5 empty] | 1.7 | [5 empty] | 1.1
[5 empty] | 2.4 | [5 empty] | 1.2
[5 empty] | 2.2 | [5 empty] | 1.1
[5 empty] | 2.3 | [5 empty] | 1.3
AVG: | 68.2857 | AVG: | 4.6429 | AVG: | 2.0385 | AVG: | 68.8571 | AVG: | 4.7143 | AVG: | 1.2154