## SR
FISHWAY STATUS REPORT | [5 empty] | THE DALLES/JOHN DAY DAM
Date: 2/2/2009 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 1/25 - 1/31/2009 | [5 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.298.7406
Fish ways are inspected once daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: | 7 | Temperature: |  | 37.6429 | F
|  |  | Out of Criteria | Limit | Comments |  | Secchi: | 3.5 | Ft.
NORTH FISHWAY |  |  |  |  | Dewatered for winter preventive maintenance; return to service 2/28.
Exit differential |  |  |  | ≤ 0.5'
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir N1 |  |  |  | depth (≥ 8')
Entrance weir N2 |  |  |  | Closed | Bulkhead installed
PUD Intake differential |  |  |  | ≤ 0.5'
EAST FISHWAY |  |  |  |  | Fish unit 1 OOS. Fish unit 2 running at 16.4 MW. Weirs set according to FPP.
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 3 | Per forebay | Auto adjusts at 1' increments. Weir 156 OOC; TDE working on unit.
Weir 158-159 differential |  |  | 0 | 1.0' ± 0.1'
Count station differential |  |  | 0 | ≤ 0.3' | Raked down stream picket leads of aquatic vegetation 1/26, 1/31.
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Junction pool weir JP6 |  |  | 0 | depth (≥ 7') | Manually adjusted as needed.
East entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  |  | 0 | No criteria | Manually adjusted as needed for criteria differential. Presently closed.
Entrance weir E2 |  |  | 0 | depth (≥ 8') | Set at 8.5' depth.
Entrance weir E3 |  |  | 0 | depth (≥ 8') | Set at 8.5' depth.
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 1.95 average in fps.
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 2 | depth (≥ 8') | Set at 8.2'. OOC at 7.9'. One fish unit operation.
Entrance weir W2 |  |  | 2 | depth (≥ 8') | Set at 8.2'. OOC at 7.9'.
Entrance weir W3 |  |  | 0 | No criteria | Manually adjusted as needed
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  |  | 0 | depth (≥ 8') | Closed for 1 fish unit operation
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Set at 10.5' depth.
JUVENILE PASSAGE
Sluice gate operation |  |  |  | units 1,5,18 | End gate closed; sluice gate 1-1 and 18-3 open per FPP.
Turbine trash rack drawdown |  |  |  | <1.5', wkly | Starts again April 1st
Spill volume |  |  |  | 0 | Spill on seal.
Spill Pattern |  |  |  | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: | 7 | Temperature: |  | 38.1429 | F
|  |  | Out of Criteria | Limit | Comments |  | Secchi: | 4 | Ft.
NORTH FISH WAY |  |  |  |  | Dewatered for winter preventive maintenance. Return to service mid February.
Exit differential |  |  |  | ≤ 0.5'
Exit hydraulic weirs |  |  |  | Per fore bay
Count station differential |  |  |  | ≤ 0.3'
Weir crest depth |  |  |  | 1.0' ± 0.1'
Entrance differential |  |  |  | 1.0' - 2.0'
Entrance weir EW1 |  |  |  | depth (≥ 8')
Entrance weir EW2 |  |  |  | No criteria
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per fore bay | Set at mid fore bay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  |  | 0 | depth (≥ 8') | Average depth 8.4'.
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.35 average in fps.
Bay 1 differential |  |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  |  | 0 | depth (≥ 8') | Average depth 8.6'.
Entrance weir NE2 |  |  | 0 | depth (≥ 8') | Average depth 8.9'.
JUVENILE PASSAGE
Fore bay/bypass conduit differential |  |  | 0 | 4.0' - 5.0' | Adjustment to 1/3 orifices open, rotated twice weekly.
Submersible traveling screens |  |  | 0 | visual inspect | Monthly inspection schedule
Turbine trash rack drawdown |  |  |  | <1.5', wkly
Vert barrier screen drawdown |  |  |  | 0
Spill volume |  |  |  | 0 | Spill on seal.
Spill pattern |  |  |  | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | SMF dewatered 12/1/08, return to service ~ 4/1/09.
Maintenance: SMF regular winter preventive maintenance underway in preparation for the water up on 1 April.
Switch gate removed in preparation for the design, procurement, and installation of the new bladder seal which will eliminate excessive leakage.
Other work includes: removing loose epoxy flakes from the elevated chute; crest gate limit switches calibration, and cleaning of adult fish/debris
separator tub in preparation for its repainting. One leaking expansion joint immediately upstream of primary dewatering structure is scheduled to
be sealed by JD structural crew.
OTHER ISSUES:
THE DALLES
Maximum daily bird observations:
North ladder exit - 42 double crested cormorants.
East ladder entrance - six mergansers, five double crested cormorants, two Canada geese.
Westrick park - eight Bald Eagles
Powerhouse tailrace -25 gulls
Fisheries coordinating with District / wall contractor to ensure that the tailrace avian lines are replaced before the start of spill season on 10 April.
They were removed last year to facilitate access for the wall contractor equipment and need to be reinstalled for this passage year.
USDA has agreed to reinstall 19 lines on 8 & 9 April (very short window, thanks to Mr. Dillon for his expertise and efforts!)
Maintenance:
TD east fishway continues in one unit operation mode due to the ongoing F1 overhaul. West entrance boarder line with W1& 2 weirs set close to 8.0'
to maximize its differential. South entrance set for one weir operation; it can't be set shallow due to high differential problems there.
TD north in-water maintenance ongoing. JDS is coordinating with the wall contractor for a two day window to replace N1 weir's damaged cable.
Will return back to service shortly after this task is completed (next week?)
The Dalles spill wall construction's first 300' section of the wall from the dam out across the spillway is ~ 75% complete with fifteen of it's twenty
200 ton concrete sections in place. Work on a leveling slab for the next 530' section is ~ 50 % complete.
Research: Battelle sluiceway kelt/adult fallback study fall portion completed Dec 15. Spring half of study will continue on 1 Mar -9 April.
The University of Idaho's lamprey PIT tag detection crew continues with their maintenance of the ladder's exit antennas.
JOHN DAY
Birds: Very few birds observed around the project.
New comprehensive tailrace avian line's grid has been designed by District and the contract is out. Project crews provided critical safety
recommendations to assure that it will successfully meet all our requirements. Its expected installation is in March and before the start of spill
season on 10 April.
Maintenance:
JD North in-water maintenance ongoing. Fisheries continues coordinating with CRITFC and Umatillas to provide support for their lamprey passage
investigations. A contractor (Cramer Associates) is planning to install underwater cameras between the CS picketed leads to monitor lamprey there.
Expected to be performed the week of 9 Feb. Umatillas coming over on 12 Feb for an inspection to look at potential lamprey passage improvements.
South ladder meeting all passage criteria with the two AWS turbines in service, the third continues on long term overhaul (ERTS is 1 March '10.)
Fisheries has completed 2008 Annual Passage Report summarizing yearly fish way inspections, dewatering results and all significant events.
The results are demonstrating the high criteria compliance and excellent fish passage conditions overall.
Research:
Fisheries assisting Portland District with planning of 2009 TSW biological evaluations to be performed during upcoming juvenile fish passage
season April to July. Planning meeting scheduled for 2/5.
Battelle acoustic tags' contractor coordinating with the forebay BRZ boat work to calibrate their powerhouse and spillway hydrophones.
Scheduled for 2/3- 2/6. Miro holding spillway safety clearance.
The University of Idaho's lamprey PIT tag detection crew continues with their maintenance of the ladder's exit antennas.
approved by;
Tamera Armstrong/s/ project manager The Dalles Dam
Kimberley Oldham/s/ project manager John Day/Willow Creek Dams

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: | 38 | Secchi: | 4 | Velocity: | 1.95 | Temp: | 38 | Secchi: |  | Velocity: | 2.35
| 37 |  | 3.5 |  |  |  | 38 |  | 4.5
| 37 |  | 3 |  |  |  | 38 |  | 4.5
| 38 |  | 4 |  |  |  | 38 |  | 4
| 37.5 |  | 4 |  |  |  | 38 |  | 4
| 38 |  | 3 |  |  |  | 38 |  | 3
| 38 |  | 3 |  |  |  | 39
AVG: | 37.6429 | AVG: | 3.5 | AVG: | 1.95 | AVG: | 38.1429 | AVG: | 4 | AVG: | 2.35