## SR
FISHWAY STATUS REPORT | [6 empty] | THE DALLES/JOHN DAY DAM
Date: | 2007-03-12 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 03/04 - 03/10/2007 | [6 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.296.7406
Fishway inspections twice daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 41.14 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.3 | Ft.
NORTH FISHWAY |  |  |  |  | PUD turbine in service.
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 1 | 1.0' ± 0.1' | Set at 1.0'. Automation corrected.
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8')
Entrance weir N2 |  |  |  |  | Closed.
PUD Intake differential |  |  | 0 | ≤ 0.5'
EAST FISHWAY |  |  |  |  | Both fish units in service.
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 0
Weir 158-159 differential |  |  | 0 | 1.0' ± 0.1'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
Junction pool weir JP6 |  |  | 0 | depth (≥ 7') | Manually adjusted as needed >7' below tailwater
East entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  |  | 0 |  | Manually adjusted as needed
Entrance weir E2 |  |  | 0 | depth (≥ 8')
Entrance weir E3 |  |  | 0 | depth (≥ 8')
Collection channel velocity |  |  | 6 | 1.5 - 4 fps | 1.4643 | average in fps. | Corrective adjustments not possible.
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 0 | depth (≥ 8')
Entrance weir W2 |  |  | 0 | depth (≥ 8')
Entrance weir W3 |  |  |  |  | Closed
South entrance differential |  |  | 1 | 1.0' - 2.0' | Manually adjusted for correction.
Entrance weir S1 |  |  | 14 | depth (≥ 8') | Manually adjusted for differential. Compensation for missing S2 weir.
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Weir removed for repair. Expected return Apr 15. Approx depth 15' to entrance floor.
ICE/TRASH SLUICEWAY |  |  |  |  | Open for juvenile passage Apr 1.
Sluice gate operation |  |  |  | 1, 5, 18 | 1-1 & 18-3 open End Gate closed
SPILLWAY |  |  |  |  | Closed
Pattern |  |  | 0 | per FPP
UnitPriority |  |  | 0 | per FPP
1% Efficiency of turbines |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 40.8571 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.7857 | Ft.
NORTH FISHWAY |  |  |  |  | Three of 6 pumps in service.
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | OpenFB263' | Closed.
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
Entrance differential |  |  | 5 | 1.0' - 2.0' | EW1 weir manually adjusted. Maintenance programing automation.
Entrance weir EW1 |  |  | 3 | depth (≥ 8') | Manually adjusted.
Entrance weir EW2 |  |  |  |  | Closed.
SOUTH FISHWAY |  |  |  |  | Two of 3 turbine/pumps in service. Maintenance repairing broke wicket link in third.
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | low/mid/high | Set at mid forebay range.
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1' | Set at 1.0'.
South entrance differential |  |  | 0 | 1.0' - 2.0' | Borderline criteria due to 2 of 3 trubines on.
Entrance weir SE1 |  |  | 5 | depth (≥ 8') | Adjusted.
Collection channel velocity |  |  | 14 | 1.5 - 4 fps | 0.96486 | average in fps. | Low velocity from 2 of 3 turbines on.
Bay 1 differential |  |  | 1 | 1.0' - 2.0' | Fish units off for dive operation Mar 8
N.entrance PH(Bay 19)differential |  |  | 1 | 1.0' - 2.0' | Fish units off for dive operation Mar 8
Entrance weir NE1 |  |  | 1 | depth (≥ 8') | Adjusted
Entrance weir NE2 |  |  | 1 | depth (≥ 8') | Adjusted
JUVENILE BYPASS SYSTEM |  |  |  |  | 1/3 orifies open, rotated twice weekly. Return to full operation Apr 1.
Forebay/conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | inspected | STS installation prior to Apr 1
SPILLWAY |  |  |  |  | Closed
Pattern |  |  | 0 | per FPP
Unit Priority |  |  | 0 | per FPP
1% Efficiency of turbines |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | Dewatered for the season. Return to 24/7 operation Apr 2.
Maintenance: Regular PMs and specific repairs are underway.
Full flow PIT detection flume installation on schedule. Final inspection scheduled for Mar 20.
OTHER ISSUES:
THE DALLES
Low gull numbers. Moderate cormorant numbers roosting on north forebay towers, but not observed around dam during day.
USDA avain line modification contract scheduled for Mar 14. Plans include concentrating coverage over spillbays 1-10 and removing lines from
south spillbays. USDA avian hazing contract to begin May 1 with 5 day/week coverage. Late start and coverage reduction due to staff shortage.
Calibration check Mar 2. All weir and stillwells within limits.
South entrance weir S2 remains out of service and removed for repairs. Expected return mid Apr. Criteria differential achieved with S1 adjustments.
UofI adult radiotelemtry downloads continue. Minimal other research expected for '07 season.
JOHN DAY
Low gull numbers. USDA avian line repairs over spillway scheduled for Mar 13. USDA avain hazing contract to begin May 1 with reduced coverage.
Calibration check Mar 2. All weir and staff gauges within limits.
South fish turbine/pump rehab planning and preparation underway. First of 3 to start winter outage '07/'08. Operational adjustments being explored
in preparation of 2 turbine operation during '08 passage season.
UofI adult radiotelemtry downloads continue. Minimal other research expected for '07 season.
Approved by;
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## AVGS
The Dalles: | [5 empty] | John Day:
Temp: | 40 | Secchi: | 5.5 | Velocity: | 1.5 | Temp: | 41 | Secchi: | 6 | Velocity: | 1
| 41.9 |  | 5 |  | 1.5 |  | 41 |  | 6 |  | 1.1
| 41.8 |  | 5 |  | 1 |  | 40 |  | 5.5 |  | 0.9
| 41 |  | 5.5 |  | 1.48 |  | 41 |  | 5.5 |  | 0.8
| 41 |  | 5.5 |  | 1.41 |  | 41 |  | 6 |  | 1
[5 empty] | 1.31 |  | 41 |  | 6 |  | 1
[5 empty] | 1.4 |  | 41 |  | 5.5 |  | 1
[5 empty] | 1.4 | [5 empty] | 0.91
[5 empty] | 1.5 | [5 empty] | 1
[5 empty] | 1.7 | [5 empty] | 0.498
[5 empty] | 1.5 | [5 empty] | 1.1
[5 empty] | 1.8 | [5 empty] | 1.2
[5 empty] | 1.6 | [5 empty] | 1
[5 empty] | 1.4 | [5 empty] | 1
AVG: | 41.14 | AVG: | 5.3 | AVG: | 1.4643 | AVG: | 40.8571 | AVG: | 5.7857 | AVG: | 0.96486