## SR
FISHWAY STATUS REPORT | [6 empty] | THE DALLES/JOHN DAY DAM
Date: | 2008-03-31 | [7 empty] | TD/JD/WC Project-Fisheries
Inspection Period: |  | 03/23 - 03/29/2008 | [6 empty] | P.O. Box 564
The Dalles, OR 97058-9998
Phone: 541.298.7406
Fishway inspections twice daily.
The Dalles Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 44 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.2857 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir N1 |  |  | 0 | depth (≥ 8') | Set at 9.5' depth
Entrance weir N2 |  |  |  | Closed | Bulkhead installed
PUD Intake differential |  |  | 0 | ≤ 0.5'
EAST FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Removable weirs 154-157 |  |  | 0 | Per forebay | Auto adjusts at 1' increments
Weir 158-159 differential |  |  | 0 | 1.0' ± 0.1'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Junction pool weir JP6 |  |  | 0 | depth (≥ 7')
East entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir E1 |  |  | 0 | No criteria | Manually adjusted as needed for criteria differential
Entrance weir E2 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Entrance weir E3 |  |  | 0 | depth (≥ 8') | Set at 12.5' depth
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.4111 | average in fps. | #'s via SR0322, Not performed This week
West entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir W1 |  |  | 0 | depth (≥ 8') | Set at 9' depth
Entrance weir W2 |  |  | 0 | depth (≥ 8') | Set at 9' depth
Entrance weir W3 |  |  | 0 | No criteria | Manually adjusted as needed
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir S1 |  |  | 0 | depth (≥ 8') | Set at 8.5' depth
Entrance weir S2 |  |  | 0 | depth (≥ 8') | Set at 8.5' depth
JUVENILE PASSAGE
Sluicegate operation |  |  | 0 | units 1,5,18 | Sluicegates 1-1 and 18-1 open, endgate closed
Turbine trashrack drawdown |  |  | 0 | <1.5', wkly
Spill volume |  |  | 0 | 40%, 24hr | On Seal
Spill Pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 0 | per FPP
Turbine 1% Efficiency |  |  | 0 | per FPP
John Day Dam |  |  | Inspections | Criteria | Total Number of Inspections: |  | 14 | Temperature: |  | 44.4286 | F
|  |  | Out of Criteria | Limit | Comments |  |  | Secchi: | 5.7143 | Ft.
NORTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Exit hydraulic weirs |  |  | 0 | Per forebay | Set for forebay >263'
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
Entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir EW1 |  |  | 0 | depth (≥ 8')
Entrance weir EW2 |  |  | 0 | No criteria | Weir closed
SOUTH FISHWAY
Exit differential |  |  | 0 | ≤ 0.5'
Hydraulic weir positions |  |  | 0 | Per forebay | Set at mid forebay range
Count station differential |  |  | 0 | ≤ 0.3'
Weir crest depth |  |  | 0 | 1.0' ± 0.1'
South entrance differential |  |  | 0 | 1.0' - 2.0'
Entrance weir SE1 |  |  | 0 | depth (≥ 8')
Collection channel velocity |  |  | 0 | 1.5 - 4 fps | 2.6422 | average in fps. | #'s via SR0322, Not performed This week
Bay 1 differential |  |  | 0 | 1.0' - 2.0'
N.entrance PH(Bay 19)differential |  |  | 0 | 1.0' - 2.0'
Entrance weir NE1 |  |  | 0 | depth (≥ 8')
Entrance weir NE2 |  |  | 0 | depth (≥ 8')
JUVENILE PASSAGE
Forebay/bypass conduit differential |  |  | 0 | 4.0' - 5.0'
Submersible traveling screens |  |  | 0 | visual inspect | Monthly inspection schedule
Turbine trashrack drawdown |  |  |  | <1.5', wkly | Range;
Vert barrier screen drawdown |  |  |  |  | Range;
Spill volume |  |  | 0 | 30%, 24hr | On Seal
Spill pattern |  |  | 0 | per FPP
Turbine Unit Priority |  |  | 5 | per FPP |  | MU 4 oos
Turbine 1% Efficiency |  |  | 0 | per FPP
SMOLT MONITORING FACILITY
Operation: | Preparing for return to service Apr 1.
Research: NOAA crew is coordinating for the full flow PIT tag detection test; they are scheduled to release 2000 fish into transport flume on 4/3.
Maintenance: Preventative maintenance complete. Work continues on PLC upgrade as funds become available.
OTHER ISSUES:
THE DALLES
Avian predators numbers continue to be low which is normal in winter.
No new avian lines will be added this year due to ODOT restrictions on attaching them to TD bridge. USDA contract for hazing predators during the
upcoming passage season is pending approval.
Maintenance: Navlock winter outage successfully ended on 3/22.
MU4 was dewatered on 3/27. No fish were found in either scroll case or draft tube.
Fisheries setting up fish counting equipment in preparation for the start of counting season on 1 April.
Calibration: E-3 PLC out of calibration. TR Requested. Depth within criteria. All other measurements within acceptable limits.
Research:
UofI adult radiotelemetry crew downloading their ladder receivers weekly.
JOHN DAY
Avian predators numbers continue to be low which is normal in winter.
USDA crew installed additional avian lines to cover the vulnerable areas downstream of the spillway where bird predation was noted to be high in
the past years. |  | USDA bird hazing contract for May through July was sent to contracting for approval.
Maintenance:
North ladder's counting station got a fresh coat of paint in preparation for the start of counting season on 1April.
Orifice 9a inop, TR requested (03/28). Conduit PLC inop, TR requested (03/29)
Calibration: Conduit ooc at -0.6, will continue to monitor
Gatewells Drawdown: Calculations well within criteria
Research: Two TSWs were delivered on 3/23 and then were subsequently installed in spillway bays 15 & 16 by 3/26. TSW functional testing was
performed 3/26 through 3/28. Baseline Industrial (contractor) installed two fish release pipes in bays 16 & 17 in preparation for the next week's
Normandeau's direct survival testing scheduled for 4/1 - 4/4.
UofI adult radiotelemetry crew downloading their ladder receivers weekly.
Normandeau direct survival test crew arrived on 3/27 and started setting up for the next week fish releases.
USGS cut the three old fish release pipes and hauled them off the project as part of their cleanup effort.
Coordinating with Battelle for their acoustic tag tacking study scheduled for late April through mid July. Two office trailers are expected to be
delivered and set up on the forebay deck the next week.
Gene LaDouceur /s/
Project Manager
The Dalles/John Day/Willow Creek

## AVGS
The Dalles: | [6 empty] | John Day:
[6 empty] | BAY | [6 empty] | Bay(s)
Temp: | 44 | Secchi: | 4 | Velocity: | 1.887 | 1 | Temp: | 44 | Secchi: | 4 | Velocity: | 2.6087 | 2 - 4
| 44 |  | 4 |  | 1.8083 | 2 |  | 45 |  | 6 |  | 2.8125 | 4 - 6
| 44 |  | 6 |  | 2.0186 | 3 |  | 45 |  | 6 |  | 2.4658 | 6 - 8
| 44 |  | 5.5 |  | 2.17 | 4 |  | 45 |  | 6 |  | 2.7692 | 8 - 10
| 44 |  | 6 |  | 1.8468 | 5 |  | 44 |  | 6 |  | 2.6866 | 10 - 12
| 44 |  | 5.5 |  | 1.8468 | 6 |  | 44 |  | 6 |  | 2.4658 | 12 - 14
| 44 |  | 6 |  | 2.17 | 7 |  | 44 |  | 6 |  | 2.6087 | 14 - 16
[5 empty] | 2.0186 | 8 | [5 empty] | 2.9508 | 16 - 18
[5 empty] | 1.887 | SS | [5 empty] | 2.671
[5 empty] | 1.9727 | 9
[5 empty] | 1.887 | 10
[5 empty] | 2.2256 | 11
[5 empty] | 2.1171 | 12
[5 empty] | 2.2256 | 13
AVG: | 44 | AVG: | 5.2857 |  | 2.4111 | 14 | AVG: | 44.4286 | AVG: | 5.7143
[5 empty] | 2.2842 | 15
[5 empty] | 2.17 | 16
[5 empty] | 1.9727 | 17
[5 empty] | 2.0667 | 18
[5 empty] | 2.0667 | 19
[5 empty] | 2.1171 | 20
[5 empty] | 2.2256 | 21
2.0634