U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#4-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  March 21 – 27, 2008

## Turbine Operation

McNary had 11 to 13 turbine units available for power generation this week.  On March 24, turbine unit 14 returned to service after headgate maintenance in slot 14A was completed.  Also on March 24, turbine units 9 and 10 were removed from service for fish screen installation and semi-annual maintenance.  Turbine unit 9 remained out of service for a couple more days after transformer oil from T5 was noted in slot 9C and in the adjacent slots. The additional outage time was needed to remove traces of oil and to locate and examine the source.  On March 25, turbine units 11 and 12 were taken out of service 5.3 hours each for ESBS installation and semi-annual maintenance.  Turbine units 13 and 14 were concurrently out of service for USGS antenna installation and other work for 5.3 and 2.5 hours respectively.  From March 24 to 26, either unit 13 or 14 had to be in standby due to load restrictions on transmission line 6.  Both turbine units 13 and 14 were placed out of service 10.8 hours each to permit the completion of transmission line 6 maintenance and semi-annual turbine unit maintenance.  On March 27, turbine unit 14 was taken out of service for seven hours in support of fish screen installation.  On March 21 and 24 through 27, units operated outside the soft one percent criterion for a short time.  The hard constraint one percent criteria will begin April 1.

## Adult Fish Passage Facilities

The McNary fisheries biologist performed measured inspections of the adult fishways on March 21, 24 and 26.  The Washington ladder was not examined March 26 due to time constraints.  Visual fish counts will resume April 1.

### Fish Ladders:  Both ladders met all Fish Passage Plan criteria this week.  No alarms were recorded.  Both ladders exit set points were checked during every inspection and no changes or adjustments were necessary.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points met criteria this week.  Oregon ladder inspection points out of criteria included the north powerhouse pool differential on March 24 (0.9 feet); NFEW2 and NFEW3 on March 26 (slightly out of criteria at 8.9 feet); and SFEW1 and SFEW2 (8.8 to 8.9 feet).  The south pool differential remained in criterion all week.  Although automatic control printouts are not yet available for examination, the technical staff is making progress.  Water velocity meter calibration has not been completed, so readings are not yet available.  Surface channel velocities are measuring approximately 1.3 feet per second.

Auxiliary Water Supply System:  Fish pumps 2 and 3 operated all week with a blade angle of approximately 30 degrees.  Fish pump 1 is not serviceable due to an oil leak.  The juvenile facility is not yet supplying the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had two interruptions on March 26 totaling 3.3 hours due to the transmission line 6 outage and line switching,

#### Juvenile Fish Passage Facility

The facility remains shut down for winter maintenance, which is nearing completion.  The collection channel remains in emergency bypass.  ESBS installations were completed March 27.  Primary bypass operations are slated to begin March 31.  The official spring bypass season will begin April 1.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains light to moderate.  Although no trash rack cleaning occurred this week, differentials are being monitored.  From March 21 to 24, the emergency bulkhead was installed in slot 14A for headgate work.  From March 24 to 28, transformer oil was removed from the slots associated with turbine units 9 and 10.  This fluid has apparently originated from a transformer vault storm drain that had been inadvertently left open.  The oil was removed and the problem corrected by closing the drain valve and the placement of safe clearance tags to prevent future mishaps.  A slight oil sheen observed on the forbay surface quickly dissipated.  Most of the fluid was removed in the first two days of cleanup.  No oil drips or sheens have been observed in any other locations this week.

ESBSs/VBSs:  ESBSs were installed in turbine units 9 through 12 and 14 this week by March 27.  A full complement of fish screens are now in place.  The fish screen in slot 1C remains in transducer bypass mode.  VBS monitoring reveal no differentials out of criterion even when turbine units were operated at 80 megawatts.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The channel remains in emergency bypass with 42 to 43 opened orifices.  Since slot 14A was “bulkheaded” during headgate maintenance, orifices in slot 14A were closed and alternate orifices were opened in slot 14B until maintenance was completed.  From March 24 to March 27, orifices in slot 9C slot were closed as a precautionary measure due to the oil cleanup in that slot.  On March 25, from 0700 to 1100 hours, all orifices were closed in support of USGS antenna installation.  Project personnel also noted on March 25 that an orifice in slot 8C was found halfway open.  Normal orifice operation resumed after the valve actuator serviced along with two other orifice actuators later in the week.  One orifice debris blockage was noted and cleared this week.  None of the above mentioned problems appeared to seriously impact fish or collection/bypass system operation.  The dewatering structure remains dry as bulkheads are currently in place.

Transportation Facility:  Winter maintenance is nearing completion.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by control room data, which runs from 0000 to 2400 hours each day.  On April 1, the smolt monitoring staff will start recording data from 0700 to 0700 hours each day.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 155.4 | 102.9 | 0.0 | 0.0 | 43 | 42 | 6.0 | 4.3 |

*Unit 1’s scroll case temperature.

Other

On March 31, the water cannon at the bypass outfall will become fully functional.  Bird counts will resume April 1 with the start of the spring bypass season.  A few gulls, grebes, cormorants, and mergansers were observed during various inspections.  USGS and other agencies continue preparations for the upcoming season.  The zebra mussel monitoring stations are deployed.  No zebra mussels were noted this week.

Project:  Ice Harbor

# Biologist: Mark F. Plummer

Dates:  March 21 – 27, 2008

## Turbine Operation

Turbine units 1 – 5 were available for operation this period.   Turbine unit 6 is out of service due to transformer contamination.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 21, 24, and 26.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.   North and south fish ladder picketed leads were lowered on March 28th.

### Fishway Entrances and Collection Channel:  The south shore entrance (SFE) was off sill with depths of 9.2 feet, 7.4 feet, and 8.9 feet.  The north powerhouse entrance (NFE) was off sill with depths of 9.0 feet, 8.8 feet, and 8.8 feet.  The north shore entrance (NSE) was off sill with depths of 8.6 feet, 7.2 feet, and 7.9 feet.   Fishway entrance criteria is 8 feet depth or greater.  All channel/tailwater differentials were in criteria, with the exception of March 24th when a North Channel/Tailwater differential of 0.9’ was recorded.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Two of the 3 North fish pumps were operated without problems.  North shore fish pump 2 is out of service.  South shore fish pumps 1-8 were operated without problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.  Turbine unit trash racks were raked March 24th and 25th.  Approximately 5-6 cubic yards of debris was removed.

STSs/VBSs:  STSs began to be lowered March 25th and deployment was completed March 27th with exception of turbine unit 6 which is currently out of service.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   The juvenile fish bypass was watered up on March 17.  Twenty orifices were opened and no problems were reported.  On March 20, turbine unit 6 orifices were closed due to emergency RSW repairs.  Additional orifices were opened to maintain collection channel water levels within criteria.

Juvenile Bypass Facility:  The bypass was watered up on March 17, with no apparent problems.

Fish Sampling:  The first sample is tentatively scheduled for April 4.

Removable Spillway Weir:  On March 20, the RSW was put into a partial stowed position for emergency repairs.  Repairs commenced March 24th, and completed March 27th.  An inspection of the RSW side seals is scheduled for Friday March 28th.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 45.8 | 29.6 | 0.0 | 0.0 | 43 | 43 | 5.6 | 5.6 |

*Unit 1 scrollcase temperature.

Other

The navigation lock outage which began March 8 at 0600 hours, was completed on March 22 at 2400 hours.

Project:  Lower Monumental

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  March 21 – 27, 2008

## Turbine Operation

Turbine units are being operated in soft constraint of the 1% operation criteria.  Turbine unit 6 was taken out of service on February 26 at 0730 hours for RSW installation and remained out of service through March 22.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on March 24, 25, 26, and 27.

Fish Ladders:

Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) during all inspections.

### Fishway Entrances and Collection Channel:

NSE1 and NSE2 weir gates were within depth criteria (criteria: > 8’ or on sill) throughout this period.    North shore channel/tailwater head was in criteria (1’-2’).

SPE1 weir gate was in sill criteria (criteria: > 8’ or on sill) throughout this period with depths ranging from 7.4’ to 7.7’.  SPE2 was in 2 pump criteria (criteria: > 8’, on sill, or closed during 2 pump operation).  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) throughout this period.  SSE2 was in criteria (6’ above sill).  South shore channel/tailwater head was in criteria (1’-2’).  The controls for GS-11 and GS-12 (the south lower ladder diffusers) are being repaired.

### Auxiliary Water Supply System:

### Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service due to problems with the diffuser assembly and bearing housing.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  Two pump operation is expected to extend throughout this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 32 square yards of forebay debris observed during this period.

STSs/VBSs:  STSs were installed from March 18 to 20.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass was watered up on March 19 and is operating with 18 orifices open.

Collection Facility:  The facility was watered up for testing on March 20.  A few flume joints were siliconed to stop leaks.

Transport Summary:  Not applicable.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 44.3 | 30.9 | 1.9 | 0 | 43 | 42 | 4.6 | 3.0 |

*Scrollcase temperatures.

#### Other

RSW direct injury study related activities occurred throughout this period.

Project:  Little Goose

Biologists:  Eric Volkman and George Melanson

Dates:  March 21 – 27, 2008

## Turbine Operation

Turbine units 1 through 5 were available for service throughout most of the week.  Turbine units were temporary removed from service during ESBS installations.  Turbine unit 6 remains forced out of service due to grounding error.  Operating turbine units are being operated in soft constraint of the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE fisheries biologists performed measured inspections of the adult fishway March 24, 25, 26 and 27.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  All fishway components were within criteria during the report period.  Channel to tailwater head differentials ranged between 1.22 and 1.72 feet (criteria 1.0 – 2.0 ft.).  SSE weir depths ranged between 8.20 and 8.44 feet (criteria 8.0 ft. minimum), NPE weir depths ranged between 6.62 (on sill) to 7.32 feet (criteria 7.0 ft. minimum) and NSE weir depths ranged between 6.18 and 6.24 feet (criteria 6.0 ft. minimum).  Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 2.3 and 3.0 fps at the SSE and 1.8 and 2.2 fps near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.0 and 2.6 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria throughout the report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Floating forebay debris accumulations were minimal with up to 1000 square feet located near turbine 1 and 2 intakes.

ESBSs/VBSs:  Fish screens were installed March 24 through 26.  All screens except those associated with turbine unit 6 are installed.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel, dewatering structure and flume were re-watered on March 24.  There were no problems during the water up and the system continues to be operated in primary bypass mode.

Transportation Facility:  The facility remains out of service for winter maintenance and is scheduled for water-up March 31.

Transport Summary:  Transport operations are expected to begin after April 20.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 31.90 | 23.0 | 0 | 0 | 43.0 | 42.7 | 4.8 | 4.2 |

*Ladder temperature.

Other

During inspections, observations of piscivorous birds in the vicinity of the dam included 5 gulls located in the forebay.

The Navigation Lock was returned to service on March 27 at 1115 hours following annual maintenance.

# Project:  Lower Granite

# Biologists:  Mike Halter & Kent Blevins

Dates:  March 21 – 27, 2008

## Turbine Operation

Lower Granite had turbine units 1, 3, 4, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  It is scheduled to return to service in mid-June.   On March 21, final fish screen installation activities took place on turbine units 1 and 3.  Turbine unit 3 was taken out of service from 0701-1200 hours and turbine unit 1 was taken out of service from 1112-1600 hours.  All operating turbine units were run within the established guidelines during the report week.

## Adult Fish Passage Facility

On March 24, 25, and 26 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings were within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrance weir gates were also within criteria on all inspections.  North powerhouse fishway entrance weir depths were within criteria on all inspections with the exception of the March 24 inspection when north powerhouse fishway entrance weir gate one (NPE-1) had a depth of 6.5 feet (criteria ≥ 8.0 feet).  North shore fishway entrance weir gate depths were out of criteria all week and varied between 5.6 and 5.8 feet (criteria ≥7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway transition pool ranged from 0.82 to 0.98 feet per second and averaged 0.91 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 2 were operated during the report period without any problems.

#### Juvenile Fish Passage Facility

Sampling (only) activities at the fish facility started on March 25.  All fish, including sample fish after evaluation, are being bypassed back to the river.

Forebay Debris/Gatewell Debris/Oil:  The unit 1 bulkhead slot gatewells developed an accumulation of small woody surface debris early in the report week.  The debris was removed by hand dipping on March 24.

ESBSs/VBSs:  Final ESBS installation (in units 1 and 3) took place on March 21.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Collection gallery orifices are being backflushed every 3 hours to prevent blockages.

Transportation Facility:  General fish transport operations will not begin until sometime between April 20 and May 1.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 42.0 | 32.7 | 0.0 | 0.0 | 45.7 | 45.7 | 4.0 | 3.0 |

*Scrollcase temperature.

Other

Video counts in the adult fish ladder counting room began on March 1.  The recording hours are from 0600 to 1600 hours.

The adult fish trap continued operation at a 10% random sample rate to monitor steelhead.  In addition, limited radio-tagging of steelhead took place.

Two logs were removed from the RSW on April 3.  Two brief closures last 20 minutes and 1 minute were required to clear the logs.