U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#11-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  May 9 - 15, 2008

## Turbine Operation

McNary had 13 to 14 units available for power generation this week.  On May 6, unit 4 returned to service from high Kaplan head temperatures after the packing was adjusted.  However, the unit continued to have high temperature readings and from May 13 to 14, the unit was out of service with two tests on May 14 until the packing issue was resolved.  From May 12 to 13, unit 5 was out of service due to a failed ESBS in B slot which was replaced.  Also on May 13, units 1, 2 and 3 were removed from service for ESBS camera inspections for a total of 1.2 hours.  Finally on May 14, unit 3 was down 5.6 hours for replacement of a thrust pump speed switch.  On April 1, the hard constraint one percent criteria began.  On May 12, unit 6 ran outside the criteria for a short time.

## Adult Fish Passage Facilities

On May 9, 12 and 14, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting continues and the new recording system has been working well.

### Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.  The Oregon ladder’s traveling screen alarmed and was reset once.  The Washington and Oregon ladders’ exit set points were checked once and twice respectively with a slight change were noted for the Washington ladder.

Fishway Entrances and Collection Channel:  On the Washington ladder, all points met criterion.  On the Oregon ladder, all points were also in criteria except on May 9 when NFEW3, SFEW1 and SFEW2 measured 8.8 to 8.9 feet.  Control printouts of the fish way check points can be reviewed but they do not yet print automatically.  The channel’s water velocity measured approximately 1.7 feet per second.

### Auxiliary Water Supply System:  All three fish pumps were in service this week with blade angles of 22 degrees.  The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD unit had no interruptions.

#### Juvenile Fish Passage Facility

The spring bypass season, which consists of alternating days of primary and secondary bypass, continues.  The switch occurred every morning at 0700 hours.  No primary bypass outside the schedule occurred this week.  On May 9, 11, 13 and 15 from approximately 2000 to 0000, extra secondary bypass with a sample rate of 20 to 25 percent occurred for the USGS study for a total of 9.3 hours.  For the report week, 419,268 smolts were bypassed during secondary operations.  An additional 28,866 smolts were passed for the USGS tagging samples.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains moderate.  The location of the debris changes with wind direction and flow patterns.  No trash rack cleaning occurred however differentials will continue to be monitored.  No problems were observed in the gatewell slots.

ESBSs/VBSs:  ESBS’s are installed at all units.  On May 13, the screen in 5B slot which had failed was replaced.  Later that day, the replacement screen was placed in transducer bypass mode.  Also that day, the ESBS’s in 4B and 11C slots were placed in bypass mode.  The ESBS camera inspections on May 13 at units 1, 2 and 3 revealed one problem.  The screen’s brush mechanism in 2C slot was two to three feet lower than indicated and required calibration.  VBS monitoring showed no differentials out of criterion however on May 15 a total of four screens were cleaned at units 1 and 9 as a preventative measure.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  During the week, 42 to 43 orifices were opened depending on forebay elevation.  The transition screen cleaning mechanism remains out of service until repairs can be done during the mid-season maintenance shutdown in June.  All other systems were functioning well and are being monitored including during VBS cleaning and primary bypass days.

Transportation Facility:  The spring bypass season continues with alternating days of primary and secondary bypass with all fish being returned to the river.  PIT tag detection occurred in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring only occurred on secondary bypass days.  All systems functioned well.  The primary (A and B) PIT tag slide gates remain operational for research.  With select by code, only small groups of fish will be diverted and all others will continue to use the return to river lines as they provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were being turned off and on so they were functional during secondary bypass including sampling for USGS.  For the week, ice block checks of the return to river lines removed debris from the A and B lines on four and two occasions, respectively.  On May 14, after working intermittently for five days, the freight elevator used by USGS to move their fish to the tagging trailer was repaired.  During the outage, USGS personnel used the facility visitor’s center elevator.

Transport Summary:  During spring bypass season there is no transport to report, however, on May 13, a McNary driver took a tractor and fish trailer on a test run to the new release site at Bonneville Dam.  The test revealed some areas of improvement for the site.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff with the data day running from 0700 to 0700.  On April 10 at 0001, the spill program began with 40 percent of flow being spilled.  When total spill is below 57 kcfs, the spill pattern can be altered for tugboats entering or exiting the downstream end of the navigation lock.  The TSW’s are located in bays 19 and 20.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 284.3 | 226.9 | 113.9 | 90.9 | 52.1 | 51.1 | 5.0 | 4.3 |

*Morning wet lab temperature.  Water clarity provided by control room.

Other

Bird counts continue with the tailwater being check twice a day and the forebay once per day.  The high count in the tailwater was approximately 350 gulls and ten pelicans.  The high count at the bypasses’ outfalls was three gulls and five pelicans.  Hazing personnel were on duty and the water cannon functioned well.  In the forebay area, the high count was 27 grebes and eight pelicans.  Four grebes were noted in the gatewell slots with one being removed and two passing to the collection channel and out of the system.  None were seen at the separator.  Blue herons, a group of night herons, osprey and cormorants were also seen on project.  Researchers continue their studies.

U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#11-2008

Project:  Ice Harbor

# Biologist:  Mark Plummer, prepared by Peter Ober

Dates: May 9 - 15, 2008

## Turbine Operation

Turbine units 1 – 5 were available for operation this period.   Turbine units 1 and 2 were out of service for short periods May 15 while STS inspections were performed.  Turbine unit 4 was out of service May 12 from 1628 hours to 1835 hours due to governor problems. Turbine unit 6 remained out of service.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways May 12, 14, and 15.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel:  The south shore entrance (SFE) was off sill with depths of 11.4 feet, 10.4 feet, and 11.0 feet.  The north powerhouse entrance (NFE) was off sill with depths of 11.4 feet, 11.1 feet, and 11.2 feet.  The north shore entrance (NSE) was off sill with depths of 9.7 feet, 10.8 feet, and 8.3 feet.   Fishway entrance criteria is 8 feet depth or greater.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 North fish pumps were operated without problems.  North shore fish pump 2 is out of service.  South fish pumps 1-8 were operated without problems.  From May 12th between 12:18 and 1315, the #2 south shore fish pump was shut off to repair an oil leak.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in cycle mode operation.  No problems were found on the May 5 STS inspection of turbine units 3, 4, and 5.  Turbine units 1 and 2 STSs were completed May 15, with no problems to report.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   20 orifices are open.  Orifice air cylinders are being rebuilt by fish facility maintenance.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 kcfs into the juvenile collection channel.  270 kcfs is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.

Removable Spillway Weir:  The RSW in operation.

Fish Sampling:

May 9

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 71 | 4 | 0 | 0 |
| UC-CH | 39 | 2 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 65 | 5 | 0 | 1 |
| UC-SH | 11 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 186 | 11 | 0 | 1 |

May 13

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 67 | 3 | 0 | 1 |
| UC-CH | 16 | 2 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 97 | 5 | 0 | 1 |
| UC-SH | 19 | 1 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | 2 | 0 | 0 | 0 |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 201 | 11 | 0 | 2 |

River Conditions

River conditions during the week are outlined in Table 2.

Table 2.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 68.1 | 49.3 | 49.2 | 24.1 | 53 | 51 | 6.2 | 4.8 |

*Unit 1 scrollcase temperature.

Other

No Zebra mussels were observed. On May 15, the south shore fish exit bubbler air supply was out of service from 1230 hours to 1530 hours to repair air leaks.

FISH FACILITIES WEEKLY REPORT

#11 - 2008

# Project:  Lower Monumental Dam

# Biologist(s):  Bill Spurgeon and Ken Fone

Dates:  May 9-15, 2008

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria as of April 1.  Unit 3 was out of service from May 10 at 2000 hours to May 12 at 1031 hours due to a failed PLC.  The PLC was switched with the one servicing unit one.  Unit 1 was out of service from May 12 at 1031 hours to May 13 at 1100 hours when another PLC was installed.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on May 10, 12 and 13.

Fish Ladders:

Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:

NSE1 and NSE2 weir gates were in depth criteria (criteria: > 8’ or on sill) throughout this period with the exception of a 7.9’ reading at NPE1 on May 12.   This was likely spill related and it soon corrected itself.   North shore channel/tailwater head was in criteria (1’-2’).

SPE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) throughout this period with the exception of the May 13 reading of 6.8’.  On May 10 and 12 it was in depth criteria.  Spill was likely the cause of the May 13 reading and the gate lacked only 0.4 foot from being on sill.  SPE2 was in 2 pump criteria (criteria: > 8’, on sill, or closed during 2 pump operation).  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) through this period.  On all inspections it was in depth criteria except for May 13 when it was in sill criteria with a depth of 7.8’.  SSE2 was in criteria (6’ above sill).  South shore channel/tailwater head was in criteria (1’-2’).  The controls for GS-11 and GS-12 (the south lower ladder diffusers) are being repaired.

### Auxiliary Water Supply System:

### Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service due to problems with the diffuser assembly and bearing housing.  Pump 3 is bulkheaded off to minimize water loss during two-pump operation.  Two pump operation is expected to extend throughout this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0.3 square yards of forebay debris observed during this period.

STSs/VBSs:  STSs are operating normally in cycle mode.  All installed STS screens were inspected on May 5 and 6.  No problems were found.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass was watered up on March 19 and is operating with 18 orifices open.  No problems occurred this period.

Collection Facility:  Facility operation changed to transport mode on May 12 at 1500 hours.   Fish are being barged every day.  The avian predation study by OSU continued this week as did NOAA’s research on fish passage and survival.

Transport Summary:   Sampling for species composition began on May 10 so that correction factors could be obtained to prevent breaching of holding and transport density criteria. Collection for transport at Lower Monumental began on May 12 at 1500.  The first barge was on the 13th.  No problems occurred.

River Conditions

River conditions during the week are outlined in Table 3.

Table 3.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 94.1 | 71.9 | 27.9 | 22.8 | 52 | 51 | 3.5 | 3.0 |

*Scrollcase temperatures.

#### Other

Zebra mussel monitoring stations were checked on May 2 with none found.

In taking best advantage on being forced into 2 pump operation, we have decided to bulkhead off SPE 2 and pull and rebuild the entrance.  When SPE 2 is rebuilt we will reinstall it and put it into service while bulkheading off and rebuilding SPE 1.

U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#11-2008

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

# Dates:  May 9– May 15, 2008

## Turbine Operation

Turbine units 1 through 5 were available for service throughout most of the week.  Turbine units 1 through 3 were temporary removed from service on May 12 and turbine units 2 through 5 on May 13 to perform trash rack raking.  Turbine unit 6 remains forced out of service due to grounding error.  GDACS reports indicated all turbine units operated within the 1% criteria for the entire reporting period.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway May 10, 14 and 15.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Fishway components were in criteria during the report period. Channel to tailwater head differentials during the report periods ranged between 1.18 and 1.54 feet (criteria 1.0 – 2.0 ft.).  SSE weir depths ranged between 8.22 and 8.50 feet (criteria 8.0 ft. minimum), NPE weirs rested on sill with depths ranging between 5.32 to 6.48 feet (criteria 7.0 ft minimum or on sill) and NSE weir depths ranged between 6.12 and 6.36 feet (criteria 6.0 ft. minimum).  Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 2.6 and 2.8 fps at the SSE and between 2.1 and 2.5 near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.2 and 2.3 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria throughout the report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Floating forebay debris accumulations of up to 300 square feet was observed scattered inside the trash-shear boom forebay area.  No debris or oil was observed in the gatewells during this report period.   Turbine units 1 through 5 trash racks were raked for debris on May 12 and 13.  Minimal amounts of debris were removed.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 22 open orifices.

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBS/VBS operated within criteria during the report period except for the screens in front of turbine unit 6 which remains forced out of service.  Drawdown measurements were conducted on Turbine Units 1 through 5 on May 15 all measurements were within criteria.

Transportation Facility:  The facility switched from secondary bypass to collection for transport operations on May 9 at 0700 hours.  During the week small fish sample rate was set at 0.5% while the large fish sample rate was set at 0.25%.  Daily fish smolt collection ranged between 93,618 and 309,619 for a total of 1,081,044 of which 1,079,559 were transported in barges.  Descaling and mortality rates for the 6 collection days totaled 0.41% and 0.03% respectively.   The facility and all components operated satisfactorily.  NOAA personnel collected 1,389 smolts for research over the 7 day period.

Transport Summary:  Transport operations began May 9 with the first barge departing Little Goose May 10.  On days when barges were available the facility performed direct loading operations.  On days without a barge for direct loading, fish were collected in raceways and loaded onto the 8000 series barge upon arrival.    All transport operations this report period were successfully performed.

River Conditions

Spring spill operations for juvenile fish passage continued with alternating spill patterns being performed for adult migration research.  Spill criterion was set at 30% of total river flow continuous not to exceed gas saturation set at 120% in the tailrace.

Note: Beginning April 30 at 1800 hours and ending on May 9 at 0600 hours nighttime spill for wild yearling Chinook passage using uniform spill pattern to 120% gas cap was performed.

River conditions during the week are outlined in Table 4.

Table 4.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Low | High | Low | High | Low | High | Low | High |
| 74.3 | 95.2 | 22.1 | 32.2 | 50.6 | 51.5 | 2.9 | 3.7 |

*Ladder temperature.

Other

USGS continued with adult fish passage research involving tracking hydrologic flow patterns in the tailrace.

Piscivorous bird activity increased significantly this week with observations in the vicinity of the dam of 150 to 350 gulls.  Hazing activities include the use of a bird scare propane cannon during daylight hours in the tailrace flume outfall area.  The cannon’s effective hazing range is up to approximately 500 yards.

U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#11-2008

Project:  Lower Granite

# Biologists:  Mike Halter and Kent Blevins

Dates:  May 9 - 15, 2008

## Turbine Operation

Lower Granite had turbine units 3, 4, 5, and 6 were available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service during the week for a rewind of the generator and repairs to the blade and liner.  It is scheduled to return to service in mid-June.   Unit 1 remained out of service during the week due to a thrust bearing problem and scheduled to return to service by the end of the month.  All operating turbine units were run within the established guidelines.

## Adult Fish Passage Facility

On May 9, 11, and 12 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were also in criteria during the week due to tailwater elevations in excess of 633.0 feet (at which level the gates bottom out).  North powerhouse fishway entrance weir depths were on sill during all weekly fishway inspections due to consistent tailrace pool elevations below 636.0 feet (at which depth the gates bottom out and rest on their sills).   Weir depths at the north powerhouse entrances ranged from 5.9 to 6.4 feet.  North shore fishway entrance weir gate depths were out of criteria all week and varied between 5.4 and 5.8 feet (criteria ≥7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway transition pool ranged from 0.83 to 1.08 feet per second and averaged 0.92 feet per second.

### Auxiliary Water Supply System:   Fish pumps 1 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

Due to relatively high numbers of fish passing through the system, the sample rate remained at 0.5% during the week.

Forebay Debris/Gatewell Debris/Oil:  Debris levels remained low during the week.  There were no problems with any of these structures.

ESBSs/VBSs:   No problems to report.  Video camera inspections were not conducted as planned due to problems with water in the camera lens.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Collection gallery orifices are being backflushed every 3 hours around the clock to prevent blockages.

Transportation Facility:  The fourth research barge destined to release fish near Astoria (Alternate Barge Study) departed Lower Granite on May 12.  Since the beginning of every day barging on May 2, the Skamania paired release control group (vice Astoria alternate barge release group) are being loaded onto 8000 series barges and transported with the general barged fish.  The fifth Skamania Index Study barge group departed Lower Granite on May 15.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 5.

Table 5.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 97.8 | 76.4 | 28.6 | 20.5 | 54.5 | 53.6 | 3.4 | 2.8 |

*Scrollcase temperature.

Other

Numerous juvenile fish marking operations continued during the report week.  NOAA-Fisheries personnel PIT-tagged fish for the Transportation Study, In-River Survival Study, Disease Susceptibility Study, Extra Mortality Study, Alternate Barge Study, Comparative Tag Effects Study, and Delayed Mortality Study. Personnel from the University of Washington conducted a study (Latent Mortality Study) to compare latent mortality of transported juvenile hatchery yearling Chinook to that of in-river migrating ones.  Personnel from UC Davis, University of Idaho, and PNNL conducted a study (Delayed Mortality Study) to estimate differential delayed mortality of transported and in-river migrant yearling Chinook in the lower Columbia River and Estuary.  Personnel from Fish Passage Solutions/Kintama Research loaded 100 acoustic-tagged hatchery yearling Chinook and 50 non-tagged hatchery yearling Chinook onto a fish barge on the morning of May 16.  These fish are Dworshak stock and were transported to Lower Granite from Kooskia Hatchery.

The adult fish trap operated at a 4% random sample rate during the week to monitor for spring Chinook.  The sort by code system was also operated to monitor PIT-tagged spring Chinook.