U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#19-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  July 4 – July 10, 2008

## Turbine Operation

McNary had 11 to 14 units available for power generation this week.  On July 7, units 5 and 7 were removed from service for 9-year overhaul and EBTOC installation, respectively.  Units 5 and 7 will be out of service for approximately two and one month, each.  On July 8, unit 6 was out of service two hours for work related to unit 7 and ESBS camera inspection.  Also, unit 8 was removed from service for ESBS inspection and remained out of service until the next day due to a speed switch problem.  Finally, on July 8, unit 9 was out of service a total of 1.5 hours for ESBS inspection and governor work.  The hard constraint for one percent criteria began on April 1 and remains in affect.   On July 9, units 1, 2 and 13 ran out side the criteria for a short time.  From July 5 to 7, unit 8 and 13 ran at reduced load or were in standby due to high VBS differentials.  On July 7, the VBS’s were cleaned.  On July 10, units 4, 6 and 8 also ran at reduced loads for the same reason with cleaning planned for July 11.

## Adult Fish Passage Facilities

On July 5, 8 and 9, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting and temperature monitoring of the ladders’ exits continues.

### Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders except on July 9 when the Washington ladder’s head over weir was 1.4 feet.  A set point adjustment was needed due to the low forebay level and the problem was resolved that day.   Due to an influx of milfoil, the Washington picketed leads were cleaned repeatedly.  Both ladders’ set points were check three times with the one change as noted.

Fishway Entrances and Collection Channel:  On the Washington ladder, all criterion points were met this week.  However, it was noted on July 9, that W3 required calibration.  Also, both weirs’ set points will be adjusted that day.  At the Oregon north powerhouse entrance no points measured out of criteria.  However, on July 5, NFEW2 was noted to have slack cables.  On July 7, the weir was examined.  Also, during the week, NFEW1, which is not in use, received maintenance.  On July 8 at the south powerhouse entrance, SFEW1 and SFEW2 measured 8.9 feet.  Also on July 9, the south pool differential measured 0.9 feet.  The channel’s water velocity measured approximately 1.2 feet per second.

### Auxiliary Water Supply System:  All three fish pumps were in service this week with blade angles of 22 to 24 degrees except as outlined.  On July 7 at 2125, fish pump 3 was removed from service due to cover plate high water temperatures.  The top plate pump was not working properly.  On July 8 at 0455, after this pump was primed, fish pump 3 returned to service.  Later that day at 2045, pump 3 was removed form service due to an oil leak.  On July 9 at 1551 after the leak was fixed, fish pump 3 returned to service.  With each outage and restart of pump 3, the blade angles of fish pumps 1 and 2 were adjusted.  Work on fish pump 1 is scheduled for July 11.  The juvenile facility continued to supplying the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD unit had no interruptions this week.

#### Juvenile Fish Passage Facility

The spring bypass season, which consists of alternating days of primary and secondary bypass, continues.  The switch occurred every morning at 0700 hours.  On July 9, primary bypass outside the schedule occurred for six hours for VBS cleaning.  On July 4, 6, 8 and 10, extra secondary bypass for the USGS study tagging occurred from approximately 2200 to 0045 at 10 or 25 percent for a total of 6.9 hours in order to collect subyearling chinook.  For the report week, 308,051 smolts were bypassed during secondary operations.  An additional 10,910 smolts were passed for USGS tagging collection.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains heavy with fresh debris coming in daily, accumulating in both the powerhouse and spillway areas.  The debris moves with wind direction changes.  No trash racks were cleaned and differentials will continue to be monitored.  No problems were observed.  On July 10, 5C slot was partly dewatered as part of the work at unit 5.  The slot will be watered up early next week.

ESBSs/VBSs:  ESBS’s are installed at all units.  The screens at 3A, 4B, 5B and 11C slots remain in transducer bypass mode.  On July 9, the electrical cables for the screen at 4A slot were adjusted.  ESBS camera inspections at units 6, 8 and 9 revealed no problems.  VBS monitoring revealed 16 screens out of criterion.  On July 7, 8 and 9, twelve of these screens and 13 others were cleaned.  On July 11, the four remaining VBS’s will be cleaned.  While cleaning, the riggers have been replacing retaining clips and documenting screens which may require future maintenance.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  During the week, 42 to 43 orifices were opened depending on forebay elevation.  On July 10, with the unit being out of service and the slot partly dewatered, the orifice at 5C slot was closed and a make up orifice was opened at an adjacent slot.  All systems functioned well and were monitored this week.  The rectangular screen cleaning cycle time was adjusted between 60 or 90 minutes depending on debris loads.  On July 4, the air burst system was tested and verified to be operating as programmed.

Transportation Facility:  The spring bypass season continues with alternating days of primary and secondary bypass with all fish being returned to the river.  PIT tag detection occurred in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring only occurred on secondary bypass days.  All systems functioned well.  The primary (A and B) PIT tag slide gates remain off as the return to river lines provide a better bypass route for PIT tagged fish.  On July 9, the system received scheduled testing and adjustment.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were being turned off and on so they were functional during secondary bypass including sampling for USGS tagging.  Ice block checks of the return to river lines removed debris from the A and B lines on three and two occasions, respectively.  Finally, the facility is being prepared for transport season.

Transport Summary:  During spring bypass season there is no transport to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff with the data day running from 0700 to 0700.  On April 10 at 0001, the spill program began.  On June 21, the 60/40 spill pattern was to begin but could not occur due to gas cap violations and spill in excess of powerhouse capacity until July 5 when the percent of flow to the spill was achieved at 40 percent.  On June 14, the smolt monitoring staff installed temperature probes throughout the project.  The results will be published in a separate report.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 318.6 | 264.7 | 164.9 | 107.3 | 63.7 | 62.2 | 6.0 | 4.8 |

*Morning wet lab temperature.  Water clarity provided by control room.

Other

Bird counts continue with the tailwater being check twice a day and the forebay once per day.  The high count in the tailwater was approximately 70 gulls, 70 pelicans, 45 terns and 13 cormorants.  The high count at the bypasses’ outfalls was six gulls, two pelicans and two terns.  Pelicans continue to work the quite water areas of the project.  Hazing personnel left the project early last week.  The water cannon functioned well.  In the forebay area, the high count was 26 grebes, four gulls and four pelicans with an occasional tern and osprey noted.  Due to their behavior and facility operations, grebe movements are difficult to monitor.  The four grebes from last week were joined by one more grebes for a total of five grebes noted in the gatewell slots.  Three of these passed to the collection channel leaving two in the slots.  With two grebes remaining in the collection channel from last week, the total for this week was five.  Four of these grebes passed out of the system leaving one in the channel by week’s end.  No grebes were seen at separator.  Researchers are at various stages of their work with some having concluded their studies.  Preparations for the juvenile lamprey study at the raceways’ tail screens continue.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Dates: July 4 - 10, 2008

## Turbine Operation

Turbine units 1 – 6 were available for operation most of this period.  Turbine units 2 – 6 were out of service for short periods July 7 for STS inspections and Turbine unit 1 went out of service July 8 at 0757 hours to install a new enunciator.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways July 8, 9, and 10.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel:  The south shore entrance (SFE) was off sill with a depth of 11.5 feet, on still with a depth of 9.2 feet, and off sill with a depth of 9.0 feet.  The north powerhouse entrance (NFE) was off sill with depths of 11.3 feet, 1.3 feet, and 11.4 feet.  The north shore entrance (NSE) was off sill with a depth of 8.0 feet, on sill with a depth of 7.2 feet, and on sill with a depth of 11.9 feet.   Fishway entrance criteria is 8 feet depth or greater.  All channel/tailwater differentials were in criteria, except July 9.  On this inspection, the south channel tailwater was at 2.1 feet differential due to both the south and the north powerhouse fish entrances on sill.  In addition, the north channel tailwater was at 0.6 feet due to only one north shore fish pump operating.   Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 North fish pumps were operated.  North shore fish pump 3 tripped out on lubrication alarm July 6 from 0615 hours to 1215 hours.  North shore fish pump 2 is out of service.  South fish pumps 1-8 were operated without mechanical problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs were put in constant run mode operation May 27 due to fish size at Lower Monumental Dam.  No problems were found on the July STS inspections.  August STS inspections are scheduled for August 4 and 5.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   20 orifices are open.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.  270 cfs is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.

Removable Spillway Weir:  The RSW in operation.

Fish Sampling:  Fish sampling started again July 8 with a revised permit from FCRP.

July 8

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 1 | 0 | 0 | 0 |
| UC-CH | --- | --- | --- | 0 |
| C-CH-O | 28 | 1 | 0 | 1 |
| UC-CH-O | 63 | 1 | 0 | 0 |
| C-SH | --- | --- | --- | -- |
| UC-SH | --- | --- | --- | -- |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | -- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 92 | 2 | 0 | 1 |

July 10

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 6 | 0 | 0 | 0 |
| UC-CH-O | 14 | 1 | 0 | 0 |
| C-SH | --- | --- | 0 | 0 |
| UC-SH | 1 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 21 | 1 | 0 | 0 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 90.3 | 63.6 | 59.3 | 21.5 | 63 | 58 | 4.6 | 4.6 |

*Unit 1 scrollcase temperature.

# Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates: July 4 - 10, 2008

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria as of April 1.  Units were taken out of service one at a time for STS inspection on July 9 and 10.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on July 5, 9 and 10.

Fish Ladders:

Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:

NSE1 and NSE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’).

SPE1 and SPE2 weir gates were in depth or 2-pump criteria (criteria: > 8’, on sill, or closed during 2-pump operation) throughout this period.  SPE1 was returned to service after rebuilding on July 10.  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) through this period.  SSE2 was in criteria (6’ above sill).  South shore channel/tailwater head was in criteria (1’-2’).

### Auxiliary Water Supply System:

Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service to work on diffuser assembly and bearing housing problems.  Pump 3 is bulkheaded off to minimize water loss during two-pump operation.  Two-pump operation is expected to occur throughout this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 467 square yards of forebay debris observed during this period.  There was 0-55% debris coverage in the gatewells.  Debris was dipped from the gatewells on the 7th and 10th this week.  No oil was observed.

STSs/VBSs:  STS operation was changed to continuous run mode on May 24 when an average fork length of less than 120 mm was seen in sub-yearling chinook.   July STS inspection occurred on the 9th and 10th.  No problems discovered.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is operating with 18-19 orifices open.  At least 11 orifices were found partially obstructed with debris and were backflushed to clear them out during the week.

Collection Facility:  The OSU and NOAA’s research ended on July 5.  Fish facility operators continue to vigilantly monitor and remove debris from separator exits and counter tunnels, as well as remove large amounts of debris from the raceways.

Transport Summary:   Alternate day barge transport continued through this period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 85 | 60.1 | 17.6 | 17.4 | 64 | 63 | 3.8 | 3.6 |

*Scrollcase temperatures.

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

Dates: July 4 - 10, 2008

## Turbine Operation

Turbine units 1,3,4,5 were available for service throughout this report period.  Unit 2 was taken out of service on July 5 to 1600 hours on July 7 to repair ESBS 2b.  Turbine unit 6 remains out of service due to grounding error. GDACS reports indicated all turbine units operated within the 1% criteria for the entire reporting period.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway July 4, 6, and 8.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Fishway components were in criteria during the report period. Channel to tailwater head differentials during the report periods ranged between 1.10 and 1.60 feet (criteria 1.0 – 2.0 ft.).  SSE weir depths ranged between 8.10 and 8.40 feet (criteria 8.0 ft. minimum).  NPE weirs rested on sill between 5.04 and 5.84 (criteria 7.0 ft minimum or on sill), NSE weir depths ranged between 6.06 and 6.26 feet (criteria 6.0 ft. minimum). Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 1.70 and 2.88 fps at the SSE and between 2.30 and 2.59 near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.93 and 2.00 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria throughout the report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Spill for debris removal was performed on July 8.  Most debris was removed through the spill.  Approximately 400sq. ft. remained behind inside the trash shear boom.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 22 open orifices.  Normal orifice rotation was performed (every 8 hours).

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBS/VBS associated with turbine units 1,3,4,5 operated within criteria during the report period.  ESBS 2b was raised on July 5 to replace the cleaning brush motor and returned to service on July 7 at 1600. Drawdown measurements were performed on turbine units 1, 2 and 3 on July 8.  All measurements were within proper operating criteria.

Transportation Facility:  The facility continued collection for transport operations.  Fish numbers continued to decline.  During the reporting period sample rates for small and large fish were set a 4.0%.  Daily fish smolt collection ranged between 9,075 and 16,346 with a total of 79,051 smolts collected. Descaling remained low and ranged from 0.3 to 1.0%.  Observed mortality ranged between 0.19% and 0.60%.

Transport Summary:  Alternate day transport operations continued throughout the report period.  All barge loading operations were conducted successfully.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Low | High | Low | High | Low | High | Low | High |
| 61.2 | 85.3 | 18.4 | 25.7 | 62.4 | 66.5 | 4.7 | 5.6 |

*Ladder temperature.

Other

The University of Idaho and USGS continued with adult fish passage research involving tracking of adult salmon and hydrologic flow patterns in the tailrace.

Piscivorous bird activity continued to be minimal no sightings of gulls or cormorants were observed.  USDA, Animal and Plant Health Inspections Services (APHIS) activities continued.

Project:  Lower Granite

# Biologists:  Mike Halter and Kent Blevins

Dates: July 4 - 10, 2008

## Turbine Operation

Lower Granite had turbine units 1, 3, 4, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  It is scheduled to return to service in late May 2009.  Turbine unit 4 was taken out of service at 0900 hours on July 7 for annual maintenance and a CO2 upgrade.  The estimated return to service date is July 31, 2008.  All operating turbine units were run within the established guidelines.

## Adult Fish Passage Facility

On July 4, 5, 6, and 9 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during this week’s inspections.  Weir depths at the south shore fishway entrances were also in criteria all week due to tailwater elevations in excess of 633.0 feet (at which level the gates bottom out).  The north powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet (at which level these gates bottom out).  Weir depths at the north powerhouse entrances ranged from 5.2 to 5.8 feet.   North shore fishway entrance weir gate depths were out of criteria all week and varied between 5.6 and 5.7 feet (criteria ≥7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway transition pool ranged from 0.88 to 1.10 feet per second and averaged 0.96 feet per second.

### Auxiliary Water Supply System:   Fish pumps 1 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate was reduced from 10.0% to 5.0% at 0700 hours on July 4.  Due to a drop in fish numbers, it was increased back to 10.0% at 0700 hours on July 8 and remained at that level for the duration of the report week.

Forebay Debris/Gatewell Debris/Oil:   Debris levels were moderate during the week.

ESBSs/VBSs:   There were no problems with ESBSs or VBSs during the week.  A video inspection of the turbine unit #6 screens was conducted during the week.  No problems were detected.  Video inspection of the other units is scheduled for July 15 and 17.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Collection gallery orifices are being backflushed every 3 hours around the clock to prevent blockages.  It was not necessary to dewater the separator inclined screen to remove debris this week.

Transportation Facility:  Normal fish barging operations proceeded on schedule.  Fish are being barged on the even days of the month during July.

Transport Summary:  All operations have been going smoothly.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 87.9 | 62.2 | 18.4 | 18.2 | 63.1 | 61.8 | 4.5 | 2.5 |

*Scrollcase temperature.

Other

The fish facility was taken off electrical power from 2248 hours on July 7 until 0400 hours on July 8.  This was done to accommodate eventual switching of the CO2 fire protection system from bus 2 over to bus 1.   Switching over to bus 1 will allow the fire protection system to operate by a backup generator in the event of a power outage.  The fish facility was operated in the secondary bypass mode (fish bypassed through the outfall pipe to the river) during the time frame this power outage was taking place.  Normal collection activities resumed as soon as power was restored to the facility.

NOAA-Fisheries marking operations for the Comparative Tag Effects Study continued during the report week.  Fish are being tagged twice per week during the month of June.   The goal for this study is to tag 500 fish per day on marking days.

Numerous agencies (NMFS, USFWS, NPT, USGS) conducted the study “Evaluating the Responses of Snake and Columbia River Basin fall Chinook Salmon to Dam Passage Strategies and Experiences” during the week.  Lengths and weights of fish collected in the sort by code system at Lower Granite are being taken to characterize the size during seaward migration for surrogate, production, and natural subyearling fall Chinook.

The adult fish trap operated at a 4% random sample rate during the week to monitor for summer Chinook.