U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#38-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  November 14 - 20, 2008

## Turbine Operation

McNary had 11 to 12 turbine units available for power generation this week.  Turbine unit 6 remains out of service for 9-year overhaul with an estimated return to service date of December 12, and turbine unit 12 remains out of service for external thrust bearing oil cooler work which will continue into December.  On November 20, turbine unit 2 was forced out of service after VBS damage occurred in slot A during cleaning operations (see details below).  The unit returned to service November 21 after the VBS was replaced (activity took place after the close of this report period).  Turbine units 1, 2 and 3 were placed in overnight standby status after high VBS differential readings were discovered on November 14.  This allowed the debris to “slough off” the screens.  On November 20, turbine unit 3 loading was reduced to the lower end of the 1% criteria until the next day when VBSs with high differentials were cleaned (after the end of this report period).  Other than for approximately 14 hours on November 14, all turbine units ran within the soft 1% constraint this week.

## Adult Fish Passage Facilities

On November 15, 18, and 20, the McNary fisheries biologist performed measured inspections of the adult fishways.

### Fish Ladders:  During measured inspections, both ladders met all Fish Passage Plan criteria.  On November 18, the Oregon exit’s north traveling screen triggered an alarm and received maintenance.

Fishway Entrances and Collection Channel:  The Washington ladder met all criteria points this week, while the Oregon ladder met most weir depth and differential criteria.  Weir depths out of criteria included Oregon north powerhouse entrances NFEW2 and NFEW3 (respectively 8.8 and 8.9 feet on November 15) and the south powerhouse entrance, SFEW1 and SFEW2 (both 8.9 feet on November 15 and 18).  All Oregon ladder pool differentials measured within criteria all week except for the north pool differential which measured 0.8 feet on November 18.  Channel velocities averaged 1.8 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 2 ran all week with blade angles of 30 degrees except on November 17.  On that day, both fish pumps were out of service in support of direct current electrical ground tests.  Fish pump 3 will remain out of service until winter maintenance season when a dive contractor can clean the sills and the stop logs can be reset.  The juvenile facility continued to supply the usual 450 CFS to the north powerhouse pool until November 18 when collection channel flow was rerouted to the emergency bypass.  The Wasco County PUD turbine unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

On November 18, fall primary bypass season concluded with the start of emergency bypass.  This change helped facilitate repairs of the south side dewatering valve conduit and preparations for cold winter weather.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was light.  No trash racks were cleaned and differentials continued to be monitored.  On November 14, when turbine units were operating at 80 megawatts, the intake slots were examined and no problems were noted.

ESBSs/VBSs:  ESBSs are currently deployed in all operating turbine units.  The screen in slot 11C remains in transducer bypass mode.  ESBS camera inspections did not occur this week as the juvenile collection channel was switched to emergency bypass operations.  ESBS maintenance is occurring in slots 6A and 6C as turbine unit 6 is already out of service for overhaul.  Other than cable adjustments for the screen in slot 3A, there were no other ESBS problems to report.  As mentioned above, high VBS differentials were noted in turbine units 1, 2, and 3 on November 14.  With turbine unit 1 operating at 80 megawatts, two of the three associated VBSs exhibited out of criteria differential readings.  Although high VBS differentials were noted in turbine units 2 and 3, none of these measurements exceeded criteria.  All three turbine units were placed in standby overnight to allow the debris to slough off.  No further high differential readings were noted until November 20, at which time four screens measured out of criteria.  Two of the four screens and two other screens were cleaned that day.  The other two high differential screens mentioned above were located in turbine unit 3.  This turbine unit’s load was reduced to maintain VBS differential criteria until next scheduled cleaning (November 21).  The VBS in slot 2A was damaged during cleaning operations after the screen frame jammed in the slot, forcing turbine unit 2 out of service.  The damaged screen will be replaced on November 21 (after the close of this report period) concurrently with scheduled VBS cleaning operations.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  From November 14 to 18, the number of opened orifices ranged from 36 to 37 depending on forebay elevation.  The south dewatering valve remains out of service until the winter maintenance period.  Orifices associated with turbine units 6 and 12 were opened and closed as needed to compensate for the loss of dewatering capability and to keep the north side dewatering valve within a reasonable operational range.  The north side dewatering valve continued to regulate the channel elevation satisfactorily.  However, the valve was slow to respond to orifice adjustments and high/low water alarms briefly sounded at times with these adjustments.  On November 15, the side and rectangular screens cleaning cycle times were respectively reduced to 90 and 60 minutes due to increased debris loads.

On November 18 from 0830 to 1030 hours, the collection channel operations were partially switched to emergency bypass mode without the primary dewaterer bulkheads in place.  All dewatering systems were shut off.  Channel elevation adjustments were made by opening or closing orifices. During this time, the number of opened orifices ranged from 42 to 45.  These adjustments also triggered brief water alarms at times.  Dewaterer bulkheads were left out to allow adult salmonids to exit the collection channel through the emergency bypass slots and/or through the full flow pipe in order to reduce their numbers before the dewaterer bulkheads were re-installed.  Orifices were closed briefly and reopened twice to help evacuate adults from the channel.  Full emergency bypass operations began after the dewaterer bulkheads were re-installed on November 19 (from 1230 to 1400 hours).  Up to the night of November 19, biologists and technicians monitored the channel regularly on all shifts.  For the rest of the week, 42 to 43 orifices were in use.

On November 20, District personnel examined the unwatered south side dewatering valve conduit and found damage to the top mounting surfaces and sealing points.  Estimates are being prepared to determine whether the repair work is to be accomplished with project work forces or by contract.

Transportation Facility:  Fall primary bypass season continued until November 18, and the collection facility remains out of service.  During this time, PIT tag detection occurred only through the full flow bypass flume.  With the start of emergency bypass operations on November 19, the collection and transport facility was fully winterized and the winter maintenance season began.  No PIT tag detection occurs during emergency bypass operations.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the control room with the data day running from 0000 to 0000.  The smolt monitoring staff is no longer collecting data.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 152.6 | 90.4 | 0.0 | 0.0 | 54 | 52 | 6.0 | 6.0 |

Other

Bird counts are no longer occurring.  Casual observations suggest tailwater bird numbers are fluctuating significantly and are probably affected by out migrating juvenile shad numbers.  Gulls, cormorants and mergansers are the primary species noted.  Good numbers of gulls and night herons continue to be observed roosting or feeding at night.  Small groups of birds were seen in the area of the bypass outfalls.  Only an occasional small group of grebes was observed in the forebay.  No grebes were noted elsewhere on project.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Dates:  November 14 - 20, 2008

## Turbine Operation

All turbine units (1 - 6) were available for operation through the entire reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways November 17, 18 and 19.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria, except on November 17.  On this inspection, the north shore fish ladder depth over weir elevation was 0.9 feet.  The depth over the weir is adjusted automatically.  The operator was notified and the operation of the weir was checked.  Later, the depth was check again and it had adjusted to the 1.0 foot criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 8.1 feet, on sill with a depth of 7.4 feet, and off sill with a depth of 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.0 feet, on sill with a depth of 7.5 feet, and off sill with a depth of 8.0 feet.  The north shore entrance (NSE) was on sill with a depth of 8.3 feet, on sill with a depth of 7.3 feet, and off sill with a depth of 7.8 feet.   Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps and 7 of 8 south shore fish pumps were operated without problems.  North shore fish pump 2 remains out of service.  Replacement of the north shore fish pump 2 gearbox is scheduled to begin December 1.  When fish pump 2 is replaced and operating, north shore fish pump 1 will be removed and sent for corrective repairs to the gearbox.  This is tentatively scheduled for December 8.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in cycle run mode.  No problems found on the November STS inspections.   STSs are scheduled to be removed for annual maintenance beginning December 16.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   20 orifices are open.    No problems to report.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs flow into the juvenile collection channel.  270 cfs is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.  The juvenile fish along with the 30 cfs remaining are emptied into the tailrace.  The juvenile fish bypass is scheduled to be unwatered December 18.

Removable Spillway Weir:  RSW operation ceased with the end of summer spill for fish on August 31.  Permanent repairs to the seals on the RSW will be completed in January by divers.

Fish Sampling:  Juvenile fish sampling concluded July 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 44.1 | 23.9 | 0.0 | 0.0 | 54 | 51 | 8.4 | 8.4 |

*Unit 1 scrollcase temperature.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  November 14 - 20, 2008

## Turbine Operation

Beginning November 1, all turbine units have been operated within the soft constraint 1% operation criteria.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 17, 18 and 19.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) with the exception of 7.9’ readings at NPE2 on the 17th and 18th of November.  It is unlikely that this would affect fish passage. North shore channel/tailwater head was in criteria (1’-2’).

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’, on sill, or closed during two-pump operation) throughout this period, with depths ranging from 7.0’ to 7.5’.  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’), with the exception of a 0.6’ head on November 17.  This was reported to the powerhouse operator for correction.

### Auxiliary Water Supply System: Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service due to work on the diffuser assembly and bearing housing.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  Two-pump operation is expected to continue for the remainder of this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 174 square yards of forebay debris observed during this period.  Surface debris coverage in the gatewells ranged from 0-70%.  The one gatewell with 70% coverage was reported to the mechanical crew for correction and was dipped the next day.  No oil was observed.  The turbine unit trash racks were raked last week.

STSs/VBSs:  STS operation is in cycle mode.  Corps personnel have determined that the intake deck crane has cracked support legs.  Winter maintenance may be seriously affected as this crane is used to raise and service the STSs.  Project personnel are looking at mobile crane and funding options in hope that the screens may still be raised in support of annual maintenance.

STS inspection took place on November 12 with no problems found.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is operating with 18 orifices open.

Collection Facility:  Out of service for the winter.  Winter maintenance work is proceeding.

Transport Summary:   Out of the transport season.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 44.0 | 24.0 | 0.0 | 0.0 | 51.5 | 51 | 5+ | 5+ |

*Scrollcase temperatures.

#### Other

There were no zebra mussels observed at the monitoring stations on November 4.

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

Dates:  November 14 - 20, 2008

## Turbine Operation

Turbine units 1, 2, 3, 5, and 6 were available for service throughout this report period.  Turbine unit 2 was removed from service on October 20 from 1400 to 1550 hours to repair overheated bearings.  Turbine unit 4 remains out of service for 6-year overhaul maintenance.  All available turbine units were operated within the soft constraints of the 1% guidelines.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 17, 18 and 20.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials during the report periods ranged between 1.28 and 1.82 feet (criteria 1.0 – 2.0 ft.).  SSE weir depths ranged between 8.24 and 8.28 feet (criteria 8.0 ft. minimum), NPE weir depths ranged between 7.01 and 7.24 (criteria 7.0 ft. minimum or on sill), and NSE weir depths ranged between 6.12 and 6.16 feet (criteria 6.0 ft. minimum). Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 2.7 and 2.8 fps at the SSE and ranged between 1.7 and 1.8 fps near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.0 and 2.3 fps.

Auxiliary Water Supply System:  On October 18 fish pump 3 tripped off line at 1552 hours.  The unit was returned to service at 1645 hours.  Aside from this, all three fish pumps operated within criteria during the inspections.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay and gatewell debris was minimal this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 18 open orifices.

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBS/VBS operated within criteria during the report period.

Transportation Facility:  The facility continues to operate in primary bypass mode.

Transport Summary:  Transport operations ceased November 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Low | High | Low | High | Low | High | Low | High |
| 21.2 | 45.0 | 0 | 0 | 50.2 | 51.0 | 6.0 | 6.0+ |

*Ladder temperature.

Other

The University of Idaho continued with adult fish passage research involving tracking of adult salmon and hydrologic flow patterns in the tailrace.

Piscivorous birds in the immediate vicinity of the dam were observed this week.  Up to 28 cormorants and 25 gulls were observed perched on the forebay log boom.

Advanced American Construction Company continued to work on the installation of flow deflectors under spill bays 1 and 8.  During the report period construction barges and associated vehicles and vessels were located adjacent to and under Spillway 1.

The zebra mussel substrate monitor was inspected on November 17 – no mussels were detected.

Project:  Lower Granite

# Biologists:  Mike Halter and Kent Blevins

Dates:  November 14 - 20, 2008

## Turbine Operation

Lower Granite had turbine units 4, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  This turbine unit is now tentatively scheduled to return to service near January 4, 2009, as 7 pre-startup tests (electrical and mechanical tests to be performed prior to actual turbine unit operation) were cancelled.  These tests were scheduled to take place between December 13 and December 22.  Turbine unit 3 is now projected to return to service on December 18, 2008 following a 6-yr overhaul. Turbine unit 1 is projected to return to service on February 20, 2009.  All operating turbine units were run within the established 1% guidelines.

## Adult Fish Passage Facility

On November 17, 18, 19, and 20 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained in criteria at all adult fishway entrances during the report week.  Weir depth readings at the south and north powerhouse were also within criteria during the week.  Weir depth readings at the north shore entrances continue to be sacrificed in an attempt to maintain the requisite 1.0 foot of head differential. Weir depth readings ranged from 5.6 to 5.4 feet (criterion ≥7.0 feet).   Weekly velocity readings in the adult fishway transition pool ranged from 0.96 to 0.93 feet per second and averaged 0.92 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 2 were operated during the report period.  The fish pumps were shut down on November 19 from 0927 hours to 1313 hours for non-routine maintenance in order to re-program the power management relay software on fish pump 1.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels remained low in the forebay and in the gatewells.  Minimal oil was observed in gatewell 6A during the November 17 inspection.  Oil absorbent pads were placed into that gatewell.  No oil was observed in any gatewell on subsequent inspections during the report week.

ESBSs/VBSs:  Nothing to report.  The last video inspections for the year have been completed.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Collection gallery orifices were backflushed every 3 hours around the clock to prevent debris blockages.  There were no debris problems on the separator.

Transportation Facility:  The transport facility switched to secondary bypass operation (to monitor for PIT-tagged smolts) on the morning of November 1 and continued in that configuration during the report week.  Weather permitting, secondary bypass operations will continue through mid December.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 44.10 | 21.00 | 0.0 | 0.0 | 53.5 | 50.6 | 4.5 | 4.0 |

*Scrollcase temperature.

Other

Operations continued at the adult trap.  Chinook and steelhead were diverted from the ladder at a sample rate of 10%.  Scale samples were taken from unmarked Chinook and hatchery and wild steelhead.  Trucking operations are scheduled to end on November 24 and the trap is scheduled to be un-watered for the winter on Wednesday November 26.

Fish facility personnel continued counting cormorants in the forebay and tailrace areas of the dam three days per week (morning and evening counts).  This work will continue through the fall months.

COE separator technicians continue to record fall Chinook tag information for adult fish crossing the separator at Lower Granite.  This work is in support of the WDFW Snake River Lab in Dayton, WA and will continue through the duration of extended separator operations.