U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#39-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  November 21 - 27, 2008

## Turbine Operation

McNary had 11 to 12 turbine units available for power generation this week.  Turbine unit 6 remains out of service for 9-year overhaul with an estimated return to service date of December 12.  Turbine unit 12 remains out of service for external thrust bearing oil cooler work which will continue into December.  On November 21, turbine unit 2 was returned to service at 0907 hours after the VBS in A slot was replaced.  Othe outages included turbine unit 13 (November 22, 15.7 hours, turbine bearing oil pump problem) and turbine units 10 and 11 (November 25, 45 minutes, ESBS camera inspections).

## Adult Fish Passage Facilities

On November 21 and 24, the McNary fisheries biologist performed measured inspections of the adult fishways.

### Fish Ladders:  Both ladder met all Fish Passage Plan criteria during the measured inspections.

Fishway Entrances and Collection Channel:  The Washington ladder met all criterion points this week.  On November 24, Oregon powerhouse entrances, NFEW2, SFEW1, and SFEW2 measured depths of 8.9’.  Other than the north pool differential measuring 0.7’ the same day, all remaining points were in criteria all week.  The channel velocity averaged 1.4 feet per second.

Auxiliary Water Supply System:  Fish pumps 1 and 2 ran all week with blade angles of 30 degrees.  Fish pump 3 will remain out of service until winter maintenance season when a dive contractor can clean the sills and the stop logs can be reset.  The juvenile facility is no longer supplying the usual 450 CFS to the north powerhouse pool as the collection channel flow is now routed through the emergency bypass.  The Wasco County PUD turbine unit had one interruption in service this week on November 21 from 0712 to 0902 hours.  While the PUD was off line, auxiliary water bypass/energy dissipater system functioned well.

#### Juvenile Fish Passage Facility

Emergency bypass in progress.  South side dewatering valve and conduit repairs are also in progress as is other winter maintenance.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains light.  No trash racks were cleaned and differentials continued to be monitored.  No problems were observed this week.

ESBSs/VBSs:  ESBS’s are installed at all units.  The screen in slot 11C remains in transducer bypass mode and ESBS camera inspections at turbine units 10 and 11 revealed no problems.   As mentioned above, the VBS in slot 2A was completed on November 21.  Also that day, the two remaining VBS’s which had exhibited high differential readings on November 20 were cleaned along with eight other screens nearing criteria.  Six more VBSs were cleaned November 26 as a preventative measure, though they were in criteria.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Full emergency bypass continued with 42 to 43 orifices opened during this week.  Light winter maintenance has commenced as bulkheads are in place and all systems have been shutdown.  Work on the south side dewatering valve outflow conduit continues.

Transportation Facility:  The facility has been winterized and the maintenance season is in progress.  No PIT tag detection occurs during emergency bypass.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the control room with the data day running from 0000 to 0000.  The smolt monitoring staff is no longer collecting data.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 127.8 | 99.1 | 0.0 | 0.0 | 51 | 50 | 6.0 | 6.0 |

Other

Bird counts are no longer occurring.  Casual observations suggest tailwater bird numbers are fluctuating significantly and are probably affected by out migrating juvenile shad numbers.  Gulls, cormorants and mergansers are the primary species noted.  An occasional night heron was seen.  Small groups of birds were observed in the area of the bypass’s outfall.  Only an occasional small group of grebes was observed in the forebay.  No grebes were noted elsewhere on project.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Dates:  November 21 - 27, 2008

## Turbine Operation

All turbine units (1 - 6) were available for operation the entire reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways November 24, 25, and 26.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.9 feet, off sill with a depth of 6.9 feet, and off sill with a depth of 7.4 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 8.0 feet, off sill with a depth of 6.7 feet, and on sill with a depth of 7.5 feet.  The north shore entrance (NSE) was on sill with a depth of 8.0 feet, on sill with a depth of 7.1feet, and off sill with a depth of 7.6 feet.   Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The south fish entrance weir was found to be tripped out. The operator was notified to make adjustments or repairs.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps and 7 of 8 south shore fish pumps were operated without problems.  North shore fish pump 2 remains out of service.  Replacement of north shore fish pump 2 gearbox is scheduled to begin December 1.  After fish pump 2 is replaced and operating, north shore fish pump 1 will be removed and sent for corrective repairs to the gearbox.  This is tentatively scheduled for December 8.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in cycle run mode.  No problems found on the November STS inspections.   STSs are scheduled to be removed for annual maintenance beginning December 16.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   20 orifices are open.    No problems to report.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs flow into the juvenile collection channel.  270 cfs of this flow is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.  The juvenile fish along with the 30 cfs remaining are emptied into the tailrace.  The juvenile fish bypass is scheduled to be unwatered December 18.

Removable Spillway Weir:  RSW operation ceased with the end of summer spill for fish August 31.  Permanent repairs to the seals on the RSW will be completed in January by divers.

Fish Sampling:  Juvenile fish sampling concluded July 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.8 | 15.7 | 0.0 | 0.0 | 51 | 50 | 8.4 | 8.4 |

*Unit 1 scrollcase temperature.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  November 21 - 27, 2008

## Turbine Operation

Beginning November 1, all turbine units have been being operated in soft constraint of the 1% operation criteria.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 24, 25 and 26.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.   North shore channel/tailwater head was in criteria (1’-2’).

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’, on sill, or closed during two-pump operation) throughout this period, with depths ranging from 7.0’ to 7.5’.  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections despite a calibration offset in the automated control system.  This problem was reported to the operator for correction.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).  This was reported to the powerhouse operator for correction.

### Auxiliary Water Supply System: Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service in support of work on the diffuser assembly and bearing housing.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  Two-pump operation is expected to occur throughout this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 135 square yards of forebay debris observed during this period.  Surface debris coverage in the gatewells ranged from 0-21%.    No oil was observed.

STSs/VBSs:  STS operation is in cycle mode.   Due to intake crane rebuild problems (cracking of the support legs) the crane may be out of service throughout the winter.  We are looking at mobile crane and funding options in hope that the screens may still be raised so that annual maintenance can be accomplished.

STS inspection took place on November 12 with no problems found.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is operating with 18 orifices open.

Collection Facility:  Out of service for the winter.  Winter maintenance work is proceeding.

Transport Summary:   Out of the transport season.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.3 | 16.2 | 0.0 | 0.0 | 49.5 | 48 | 5+ | 5+ |

*Scrollcase temperatures.

#### Other

There were no zebra mussels observed at the monitoring stations on November 4.

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

Dates:  November 21 - 27, 2008

## Turbine Operation

Turbine units 1, 2, 3, 5, and 6 were available for service throughout this report period.  Turbine unit 4 remains out of service for 6-year overhaul maintenance.  Turbine units were operated within the soft constraints of the 1% guidelines.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 24 and 25.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials during the report periods ranged between 1.22 and 1.60 feet (criteria 1.0 – 2.0 ft.). SSE weir depths ranged between 8.36 and 8.38 feet (criteria 8.0 ft. minimum).  NPE weir depths ranged between 7.22 and 7.26 (criteria 7.0 ft. minimum or on sill), NSE weir depths ranged between 6.16 and 6.22 feet (criteria 6.0 ft. minimum). Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 2.65 and 2.68 fps at the SSE and ranged between 2.2 and 2.3 fps near the NSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.95 and 1.98 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria during the inspections.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay and gatewell debris was minimal this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 18 open orifices.

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBS/VBS operated within criteria during the report period.

Transportation Facility:  The facility continues to operate in primary bypass mode.

Transport Summary:  Transport operations ceased November 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Low | High | Low | High | Low | High | Low | High |
| 30.4 | 13.6 | 0 | 0 | 48.5 | 48.7 | 6.0 | 6.0+ |

*Ladder temperature.

Other

The University of Idaho continued with adult fish passage research involving tracking of adult salmon and hydrologic flow patterns in the tailrace.

Piscivorous birds in the immediate vicinity of the dam were observed this week.  Up to 20 cormorants and 12 gulls were observed pearched on the forebay log boom.

Advanced American Construction Company continued to work on the installation of flip lips under Spillways 1 and 8.  During the report period construction barges and associated vehicles and vessels were located adjacent to and under Spillway 1.

Project:  Lower Granite

# Biologists:  Mike Halter and Kent Blevins

Dates:  November 21 - 27, 2008

## Turbine Operation

Lower Granite had turbine units 4, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  It is now tentatively scheduled to return to service near January 4, 2009.   Turbine unit 3 is now projected to return to service on December 18, 2008 following a 6-yr overhaul.  Turbine unit 1 is projected to return to service on February 20, 2009.  All operating turbine units were run within the established guidelines.

## Adult Fish Passage Facility

On November 24, 25, and 26 the Lower Granite fisheries personnel performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings were in criteria at all south shore and north powerhouse entrances but were slightly below criteria at the north shore entrances on all inspection dates with readings of 0.9 feet (criterion ≥ 1.0).  Problems with the automated fishway control computer or software are suspected causes.  Lower Granite electronic technical personnel are looking into this problem. Weir gates will be manually lowered to achieve criteria while this problem is being resolved. Weir depth readings were in criteria at the south shore entrances during the report week.  Weir depth readings at the north powerhouse entrances were slightly below criteria on the November 25 and 26 inspections when both gates were resting on sill with readings that ranged between 7.98 and 7.88 feet (criterion ≥ 8.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in an attempt to maintain the requisite 1.0 foot of head differential.  North shore weir depth readings ranged between 5.5 and 5.8 feet during the report week (criterion ≥ 7.0 feet).  Weekly velocity readings in the adult fishway transition pool ranged from 0.94 to 0.96 feet per second and averaged 0.95 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 2 were operated during the report period without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels remained low in the forebay.  Surface debris in the gatewells also remained low during this report week.  A slight oil sheen was observed in gatewell 6A during the November 26 inspection.  Absorbent pads were placed into this gatewell.

ESBSs/VBSs:  Nothing to report.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Starting November 21 collection gallery orifices have been backflushed every 4 hours instead of every 3 hours around the clock to prevent debris blockages in the orifices.  This operational change was made due to the continuing lack of debris in the system and favorable long term weather forecasts.

Transportation Facility:  The transport facility was switched to secondary bypass operation (to monitor for PIT-tagged smolts) on the morning of November 1 and continued in that operational configuration during the report week.  Weather permitting, secondary bypass operations will continue through mid December.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.10 | 17.5 | 0.0 | 0.0 | 51.0 | 49.4 | 4.4 | 4.1 |

*Scrollcase temperature.

Other

Trucking operations at the adult trap ended on November 24 and the trap was unwatered on November 26.  All adult trap operations are now suspended for this season.

Fish facility personnel continued counting cormorants in the forebay and tailrace areas of the dam three days per week (morning and evening counts).  This work will continue through the fall months.

COE separator technicians continue to record fall Chinook tag information for adult fish crossing the separator at Lower Granite.  This work is in support of the WDF&W Snake River Lab in Dayton, WA and will continue through the duration of extended separator operations.

Zebra mussel substrate at the adult fish ladder exit was examined during the week.  No evidence of zebra mussels was found.