U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#43-2008

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  December 19 - 25, 2008

## Turbine Operation

McNary had 12 turbine units available for power generation this week.  Turbine unit 6 remains out of service for 9-year overhaul with an estimated return to service date of December 31.  Turbine unit 14 remains out of service for external thrust bearing oil cooler work which will take approximately one month.  On December 19 and 20, ESBSs were removed from turbine units 7 through 10 with outage times totaling 16 hours.  On December 22 and 23, turbine unit 5 was out of service a total of 8.3 hours in support of fish screen removal.  The screens could not be raised previously as the crane’s hammer head was frozen.  The hammer head trips the screens to the vertical collapsed position prior to actual ESBS removal from the slots.  Finally on December 23, turbine unit 4 was out of service for four hours for ESBS removals.

## Adult Fish Passage Facilities

On December 19, 22 and 23, the McNary fisheries biologist performed measured inspections of the adult fishways.  Severe weather continued to make inspections difficult to perform.

### Fish Ladders:  During the measured inspections, both ladders met all Fish Passage Plan criteria.  On December 22, the Oregon exit weir 336 and the traveling screens triggered alarms and were reset.  Later that day, a programmable logic circuit (PLC) was used to place weir 336 in bypass mode.  An electrical technician later returned weir 336 to automatic operation.  Due to severe winter weather, ice “build-up” at the traveling screens continued to be monitored.

Fishway Entrances and Collection Channel:  The Washington ladder met all criteria points this week.  At the Oregon north powerhouse entrance, on December 22, the pool differential measured 0.9 feet.  On December 22 and 23, NFEW2 and NFEW3 measured 8.7 to 8.9 feet.  At the south powerhouse entrance, on December 19, the pool differential measured 0.9 feet.  On December 22 and 23, SFEW1 measured 8.8 feet.  For the week, SFEW2 measured 8.8 to 8.9 feet.  The channel velocity averaged 1.5 feet per second.

Auxiliary Water Supply System: Fish pumps 1 and 2 ran all week with blade angles of 30 degrees.  Pump 3 will remain out of service until winter maintenance season when a dive contractor can clean the sills and the stop logs can be reset.  The juvenile facility is no longer supplying the usual 450 CFS to the north powerhouse pool as it is in emergency bypass.  The Wasco County PUD turbine unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

Emergency bypass continues until ESBS’s removal is completed next week.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains light.  No trash racks were cleaned and differentials continued to be monitored.  No problems were observed.

ESBSs/VBSs: ESBSs were removed from turbine units 4, 5 and 7 through 10 this week.  This leaves deployed screens in turbine units 1 through 3.  Severe weather conditions continued to delay removals.  No problems with the brush mechanisms were noted as each fish screen was raised.  ESBS maintenance is in progress.  No VBSs measured out of criteria and none were cleaned.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: Full emergency bypass continued with 43 opened orifices this week.  Light winter maintenance has commenced as bulkheads are in place and all systems have been shutdown.  One slight blockage was removed from slot 3A orifice with no apparent harm to fish. Two orifice actuator handles froze up making it impossible to cycle these orifices.  A warming weather trend is expected next week which should cure the problem.  Icy conditions continue to make walking in the collection channel hazardous.

Transportation Facility:  The facility has been winterized and maintenance is in progress.  No PIT tag detection occurs during emergency bypass operations.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the control room with the data day running from 0000 to 2400 hours.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 157.9 | 107.6 | 0.0 | 0.0 | 39 | 38 | 6.0 | 6.0 |

Other

Bird counts are no longer taking place.  Casual observations indicate tailrace bird numbers are fluctuating significantly, most likely influenced by juvenile shad numbers.  Small groups of birds were observed near the bypass outfall, and no pisciverous birds were noted in the forebay.  Of interest, several over-wintering bald eagles are foraging for crippled waterfowl above and below the dam.

Project:  Ice Harbor

# Biologist:  Mark Plummer and Stephen Jeffers

Dates:  December 19 - 25, 2008

## Turbine Operation

All turbine units (1 - 6) were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways December 19.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 6.2 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 6.2 feet.  The north shore entrance (NSE) was off sill with a depth of 6.1 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps and 6 of 8 south shore fish pumps were operated until December 25.  South shore fish pump 4 and 7 are in standby mode.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in cycle run mode.  STSs are tentatively scheduled to be removed for annual maintenance beginning January 5.  With the cold weather snap, the project is concerned that raised STSs could allow accumulated water to freeze, expand and crack gearboxes.  Juvenile bypass operations will continue until STSs are raised.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  No problems to report.

Juvenile Bypass Facility:  The bypass is in operation with 20 opened orifices providing 300 cfs flow into the juvenile collection channel.  Of this, 270 cfs is dewatered and directed into the south adult fish pump chamber for additional adult fish attraction water.  The juvenile fish along with the 30 cfs remaining are routed into the tailrace.  The juvenile fish bypass is scheduled to be unwatered January 5.

Removable Spillway Weir:  RSW operation ceased with the end of summer spill for fish August 31.  Permanent repairs to the seals on the RSW will be completed in January by divers.

Fish Sampling:  Juvenile fish sampling concluded July 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 9.9 | 9.9 | 0.0 | 0.0 | 44 | 40 | 8.9 | 8.9 |

*Unit 1 scrollcase temperature.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  December 19 - 25, 2008

## Turbine Operation

Beginning November 1, all turbine units have been operated within the soft constraint 1% operation criteria.  Turbine unit 1 was taken out of service on December 1 at 0726 hours for annual maintenance and remained out of service through this report period.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on December 22 and 23.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively).  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE1 and NSE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.   North shore channel/tailwater head was in criteria (1’-2’).

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’, on sill, or closed during two-pump operation) throughout this period, with depths ranging from 7.1’ to 7.2’.  South powerhouse channel/tailwater head was within criteria (1’-2’).

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).

### Auxiliary Water Supply System: Auxiliary water supply pumps 1 and 2 are operating.  Pump 3 is out of service in support of diffuser assembly and bearing housing repairs.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.  Two-pump operation is expected for the remainder of this operating year.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil: There was an average of 47.5 square yards of forebay debris observed during this period.  Surface debris coverage in the gatewells could not be noted with STS screens up and dogged off on deck.  No oil was observed.

STSs/VBSs: STSs were raised and dogged off on deck from December 17 – 19.

Orifices, Collection Channel, Dewatering Structure, Flume: The bypass was dewatered on December 18th at 1100 hours. It is currently out of service for the winter maintenance period.

Collection Facility:  Out of service for the winter.  Winter maintenance work is in progress.

Transport Summary:   Out of the transport season.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.7 | 12.8 | 0.0 | 0.0 | 38.5 | 38 | 5+ | 5+ |

*Scrollcase temperatures.

#### Other

There were no zebra mussels observed at the monitoring stations on December 3.

The bird sprinkler was taken out of service because of ice buildup on December 15th at 0730 hours.

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

Dates:  December 19 - 25, 2008

## Turbine Operation

Turbine units 2, 4, 5 and 6 were available for service this report period.  Turbine unit 1 was forced out of service from December 17 at 1600 hours to December 22 at 1125 hours due to delayed ESBS removal.   Turbine unit 3 remained out of service since December 17 at 1600 hours also due to delayed ESBS removal.  Turbine units were operated within the soft constraints of the 1% guidelines.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on December 21 and 22.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  During inspections, channel to tailwater head differentials measured between 1.04 and 1.44 feet (criteria 1.0 – 2.0 ft.). SSE weir depths measured between 8.26 and 10.06 feet (criteria 8.0 ft. minimum).  NPE weir depths measured between 7.12 and 7.34 feet (criteria 7.0 ft. minimum or on sill), and NSE weir depths measured between 6.60 and 7.38 feet (criteria 6.0 ft. minimum). Collection channel water velocities (criteria 1.5 – 4.0 fps) ranged between 2.5 and 2.9 fps at the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.1 and 2.2 fps.    Water velocities at near the NSE were not measured this report period.

Auxiliary Water Supply System:  All three fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay and gatewell debris was minimal this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel was dewatered on December 17.

Extended Length Submersible Bar Screens/Vertical Bar Screens (ESBS/VBS):  All ESBSs except 3A through 3C are removed from service and placed in the raised position.  ESBSs 3A through 3C are scheduled to be raised December 29.

Transportation Facility:  The facility is dewatered.

Transport Summary:  Transport operations ceased November 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Low | High | Low | High | Low | High | Low | High |
| 26.4 | 13.3 | 0 | 0 | 38.5 | 38.8 | 6.0 | 6.0+ |

*Ladder temperature.

Other

Up to seven cormorants were observed in the immediate vicinity of the dam this week.

Advanced American Construction Company continued to work on the installation of flip lips under Spillways 1 and 8.

HARCON Inc. Construction Company continued staging in preparation for work on the primary dewaterer and transport/bypass flume.

Project:  Lower Granite

# Biologists: Mike Halter and Kent Blevins

Dates:  December 19 - 25, 2008

## Turbine Operation

Lower Granite had turbine units 4, 5, and 6 available for power generation at the beginning of the report week.  Turbine unit 2 remained out of service for a rewind of the generator and repairs to the blade and liner.  It is now projected to return to service on or about January 4, 2009.  Turbine unit 3 is now projected to return to service by January 5, 2009 following a 6-yr overhaul.  Turbine unit 1 is projected to return to service on February 20. 2009.  Turbine unit 1 was unwatered December 23 to inspect/repair wicket gates.  Scrollcase fish savage operations followed shortly afterwards.  All operating turbine units were run within the established guidelines.

## Adult Fish Passage Facility

On December 22, and 23, Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings at the adult fishway entrances were within criteria on both inspection dates.  Weir depth readings at the south shore and north powerhouse entrances were also in criteria during the week.  Weir depth readings at the north shore entrances continue to be sacrificed in an attempt to maintain the requisite 1.0 foot of head differential.  North shore weir gate readings ranged between 5.0 and 5.1 feet during the report week (criterion ≥ 7.0 feet).  Weekly velocity readings in the adult fishway transition pool ranged from 0.98 to 0.93 feet per second and averaged 0.96 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 2 were operated during the report period without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil: Debris levels remained low in the forebay and gatewells this week.  No oil was observed in the gatewells during weekly inspections.

ESBSs/VBSs:  Final fish screen removal operations began on December 15.  The ESBS in intake slot 4A has been jammed in its slot since December 15 when removal attempts failed.  This screen will video-inspected on December 28.  The other screens in turbine unit 4 have been successfully removed.  All other fish screens are scheduled to be removed by December 29, 2009.  Gatewell dipping to remove fish from gatewells with fish screens remaining down in the gatewell slots in units 4, 5 and 6 took place December 22.  A combined total of approximately 125 juvenile salmonids was removed from 7 gatewells and released in the tailrace in good condition.  The boat ramp at Ilia Landing is the preferred release site but the ramp was snow covered and unavailable for use.  Only 2 juvenile mortalities were recovered during gatewell dipping operations.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Nothing to report at this time.

Transportation Facility:  Transport operations will not begin until sometime in April.  Juvenile fish sampling activities are tentatively scheduled to begin on March 25.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.8 | 14.9 | 0.0 | 0.0 | 44.6 | 44.1 | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Fish facility personnel continued counting cormorants in the forebay and tailrace areas of the dam on three days per week (morning and evening counts).

Fish salvage operations conducted in Unit 1 on December 23 resulted in the recovery of no fish of any kind; however, a 5 gallon bucket full of crayfish was recovered and released to the river.