U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#4-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  March 20 – 26, 2009

## Turbine Operation

McNary had 14 turbine units available for power generation this week.  On April 1, the hard constraint one percent criteria will begin.

## Adult Fish Passage Facilities

McNary fishery biologists performed measured inspections of the adult fishways except On March 20, 23 and 26.  The Washington ladder was not examined on March 26.  Both ladders will resume visual adult fish counts on April 1.

### Fish Ladders:  Both ladders met all Fish Passage Plan criteria.  The Oregon exit weirs and traveling screens remain in manual operation as electrical system upgrades are in progress.  Operators are monitoring the exit weirs regularly, making adjustments as required and cleaning the traveling screens every four hours as needed.

Fishway Entrances and Collection Channel:  The Washington ladder met all inspection point criteria.  The Oregon ladder also met all criteria this week except on March 20 and 26 when the north powerhouse pool differential measured 0.8 feet and NFEW2 weir depth measured 8.9 feet (respectively).  Collection channel velocity averaged 1.5 feet per second this week.

Auxiliary Water Supply System: Fish pump 3 remains unwatered and out of service for the oil leak reported during the last season.  Fish pumps 1 and 2 operated all week with blade angles of 30 degrees.  The juvenile facility is not supplying the usual 450 cfs to the north powerhouse pool since the juvenile facility is currently out of service.  The Wasco County PUD turbine unit had 2 interruptions in service on March 20 totaling 4.8 hours outage time.  The bypass system functioned well during these outages.

#### Juvenile Fish Passage Facility

The juvenile facility remains shut down for winter maintenance, which is nearing completion.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was light to moderate depending on wind direction.  Gatewell debris was minimal as trash rack cleaning occurred last week.  Trash rack differentials will continue to be monitored.  A small amount of residual oil was removed from one slot with absorbent pads.

ESBSs/VBSs:  All ESBSs remain raised and maintenance is almost complete.  ESBS installations will take place between April 6 and April 16 this year, one to two weeks later than normal as a juvenile lamprey protection measure.  When fish screen installation begins, VBS monitoring will resume.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Winter maintenance is nearly concluded.  Bypass operations will begin concurrently with fish screen installations.  This week, a leaking air solenoid for the transition screen cleaning mechanism was noted and repaired.

Transportation Facility:  Winter maintenance is near completion.  The drain area for raceway 4 was cleaned and painted on a trial basis.  If this change improves loading operations, the remaining raceway drains will be painted next year.  On March 26, the facility emergency water supply line was opened for 2.5 hours so the system could be flushed and tested for leaks.  The only leak noted was located at the emergency line supply valve.  This problem was resolved after the packing was tightened.  PIT and sample gates were also tested this with no significant problems being noted.  However, a few minor air leaks were evident with the advent of warmer weather.  These leaks will be repaired in the near future.

Transport Summary:  On March 23, three out of four leased semi-tractor trucks (to be used to haul 3,500 gallon fish tankers for the season) were received and accepted.  The last truck will arrive March 30.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the control room.  Data periods run from 0000 to 2400 hours each day.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 148.6 | 103.0 | 0.0 | 0.0 | 42 | 41 | 6.0 | 4.0 |

*Unit 1’s scroll case temperature.

Other

Bird counts will resume later in the month when technicians begin shift work.  An occasional gull, grebe, cormorant, or merganser was observed during ladder inspections.  A few birds of each species now appear to over winter near the project.

The zebra mussel detection station was examined this week and no mussels were found.

The TSW was moved from spill bay 19 was to spill bay 4 this week in preparation for the for the upcoming research study season.

Project:  Ice Harbor

# Biologist:  Mark Plummer and Stephen Jeffers

Dates:  March 20 – 26, 2009

## Turbine Operation

All turbine units (1 - 6) were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 23, 24, and 26.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.   North and south fish ladder picketed leads are currently raised.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.6 feet, off sill with a depth of 8.5 feet, and off sill with a depth of 9.8 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 11.0 feet, off sill with a depth of 11.5 feet, and off sill with a depth of 9.6 feet.  The north shore entrance (NSE) was off sill with a depth of 9.0 feet, off sill with a depth of 9.0 feet, and off sill with a depth of 8.6 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill. All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  North shore fish pump 3 is out of service and is off site for repairs.  Expected return and reinstall day is tentatively April 6.  All (8) south fish pumps were available for operation.  Currently, 6 are in operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.  Turbine unit trash rack raking took place March 19 and 23.  A total of 10 to 13 cubic yards of debris were removed.   No fish were observed in the removed debris.

STSs/VBSs:  STSs were installed March 23 - 25.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass was watered up on March 16.  Twenty orifices are open.  No problems to report.

Juvenile Bypass Facility:  The bypass facility is in operation.

Fish Sampling:  The first sample is tentatively scheduled for April 7.

Removable Spillway Weir:  The RSW is in the operating position.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 58.2 | 33.5 | 0.0 | 0.0 | 42 | 42 | 3.8 | 3.6 |

*Unit 1 scrollcase temperature.

Other

Juvenile fish passage season begins April 1.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  March 20 – 26, 2009

## Turbine Operation

All turbine units are being operated in soft constraint of the 1% operation criteria.  Turbine units were rotated out of service on March 23 and 24 to accommodate STS installation.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on March 23, 24, 25 and 26.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.     North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gate was in sill criteria (criteria: > 8’ or on sill) with a depth of 7.1’ and 7.0 feet on March 26 and 25, respectively, and was in depth criteria on the remaining inspections this week.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) through this period.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed late in 2009.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded” off to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 575 square yards of forebay debris observed during this period.  No oil was observed in gatewells.

STSs/VBSs: The STS rebuild continues.  STSs were installed on March 24 and 25.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass was watered up March 18 in response to a buildup of juvenile steelhead in the gatewells.

Collection Facility:  Winter maintenance is nearly completed.  The facility will be watered up for testing the week of March 29.

Transport Summary:  Not collecting for transport.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 55.1 | 35.3 | 0 | 0 | 41.5 | 41.5 | 2.4 | 1.2 |

*Scrollcase temperatures.

#### Other

The bird deterrent sprinkler piping damaged last fall duiring a severe frost.  The sprinkler will be repaired during the week of March 29.  No birds have been observed at the bypass outfall.

There were no zebra mussels observed at the monitoring stations this month.

Project:  Little Goose

# Biologists:  Eric Volkman and George Melanson

Dates:  March 20 – 26, 2009

## Turbine Operation

Turbine units 1 through 4 were available for service throughout the week.  Turbine units 5 and 6 have been out of service since March 12 due to an electrical bus grounding error (both turbine units share the same electrical bus).  Remaining turbine units are being operated within soft constraint of the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE fisheries biologists performed measured inspections of the adult fishway March 20, 23, and 24.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  All fishway components were in criteria during the report period.  During inspections, channel to tailwater head differentials ranged between 1.12 and 1.62 (criteria 1.0 ft.).  SSE weir depths ranged between 8.12 and 8.34 feet (criteria ≥8.0 ft), NPE weir depths ranged between 7.08 and 7.34 feet (criteria ≥7.0 ft.) and NSE weir depths ranged between 6.04 and 6.16 feet (criteria ≥ 6.0 ft.).  Collection channel water velocities (criteria 1.5 fps) ranged between 2.2 and 2.7 fps near the SSE, and 1.5 to 1.8 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 1.9 and 2.2 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 3,000 square feet of floating debris was observed inside the trash-shear boom in front of turbine units 1, 2 and 3 intakes.

ESBSs/VBSs:  ESBSs 4A through 6C were lowered into position during this report period.   ESBSs 1A through 3C are scheduled to be lowered March 30 and 31.

Orifices, Collection Channel, Dewatering Structure, Flume: On March 24, 2009, the juvenile collection channel was watered up and placed into primary bypass with 18 orifices opened.  The full-flow PIT-tag detector was provisionally accepted (subject to completion of some minor repairs) by Corps construction representatives and turned over to the Little Goose personnel on March 24.  PSMFC personnel indicated some PIT-tag detection was taking place, and that some further adjustments would be needed.

Transportation Facility:  The facility was watered-up on March 24 and placed into primary bypass.  All components are operating in criteria.   Secondary bypass (separator bypass) is scheduled to start on April 1.

Transport Summary:  Transport operations are expected to begin after April 20.

TSW:  The TSW was operated during the report period to perform direct injury and survival studies.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 49.9 | 32.0 | 2.4 | 0 | 40.7 | 40.4 | 4.5 | 3.3 |

*Ladder temperature.

Other

HARCON contractors have completed installation of the pit tag detector.  HARCON is scheduled to complete upgrades to the primary dewaterer and flume outfall relocation during the 2009 – 2010 maintenance season.

The Direct Injury and Survival Study being performed by Normandeau Inc. continued on TSW/Spillway 1 and spillway 8 this week.

USGS personnel continued to install and test equipment in preparation for the Smolt Passage and Survival Study scheduled to start April 16.

Project:  Lower Granite

# Biologists: Mike Halter and Kent Blevins

Dates:  March 20 – 26, 2009

## Turbine Operation

Lower Granite had turbine units 1 – 6 available for power generation at the beginning of the report week.   Fish screen installation activities took place in all turbine units during the week with unit outages taking place as follows:  March 23, turbine unit 1 (0653 – 1056 hours); March 23, turbine unit 2 (1205 – 1629 hours); March 24, turbine unit 2 (1400 – 1618 hours); March 25, turbine unit 2 (0702 – 0950 hours); March 25, turbine unit 3 (1010 – 1408 hours); March 25, turbine unit 4 (1422 – 1639 hours); March 26, turbine unit 4 (0647 – 0804 hours); March 26, turbine unit 5 (0830 – 1315 hours); March 26, turbine unit 6 (1159 – 1639 hours).

## Adult Fish Passage Facility

On March 23, 25 and 26, Lower Granite fishery biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings were within criteria at all adult fishway entrances during inspections.  Weir depths at the south shore fishway entrances were within criteria on all inspections during the week.  Weir depths at the north powerhouse fishway entrances were either within criteria or on sill depending on the tailwater elevation.  (Whenever tailwater elevations are below 636.0 feet the north powerhouse entrances bottom out and rest on their sills.)  Weir depths at the north shore fishway entrances were out of criteria all week with readings ranging from 5.0 to 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.84 to 1.04 feet per second and averaged 0.95 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.

#### Juvenile Fish Passage Facility

Water up of the collection gallery and initiation of primary bypass at the separator began on March 23.  Sampling activities began at 0700 hours on March 25.  The initial sample rate was set at 10%.  All fish other than those being sampled are being routed directly to the river through the bypass outfall pipe (secondary bypass mode).  Sample fish are also being returned to the river.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was minimal and none was removed this week.  Trash was “hand-dipped” from several gatewells following ESBS installation.

ESBSs/VBSs:  Deployment of all ESBSs was completed during the week.  A problem developed when the crane tugger line broke during the afternoon of March 23 but repairs were made by the following day and screen installations continued unimpeded.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Nothing to report at this time.

Transportation Facility:  General transport operations will not begin until sometime between April 20 and May 1.  Research barging operations will begin sometime in early April.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 50.0 | 33.1 | 0.0 | 0.0 | 45.5 | 44.5 | 3.1 | 2.3 |

*Scrollcase temperature.

Other

Video counts in the adult fish ladder counting room began on March 1.  Recording hours are from 0600 to 1600 hours.

The adult fish trap operations continued during the week with a sample rate of 10%.

Kelt sampling activities at the Lower Granite separator are scheduled to begin on March 29.