U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#8-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  April 17 – 23, 2009

## Turbine Operation

McNary had 11 to 14 turbine units available for power generation this week.  Outages took place on April 20 (turbine unit 5, 1.3 hours, examination of the juvenile collection channel orifice 5A), April 21 (turbine units 1, 2 and 3, 1.3 hours, ESBS camera inspections), April 22 to 23 (turbine unit 12, exciter repair) and April 23 (turbine unit 1, 29 minutes, camera inspection station service unit 2 bulkhead sills).

All turbine units have been operated within the hard 1% criteria which began April 1.  Since April 21, turbine units 11 through 14 have been operating at the upper limit of the 1% criteria as part of the USGS survival study.

## Adult Fish Passage Facilities

On April 18, 20 and 23, McNary fishery biologists performed measured inspections of the adult fishways.  Visual adult fish counting continued.

### Fish Ladders:  Both ladders met all Fish Passage Plan criteria were met on both ladders except for the Oregon ladder head over weir differential on April 20 which measured 0.9 feet.  This criterion was met following manual adjustments.  The Oregon weirs and traveling screens remain in manual mode as electrical system upgrades continued.  Operators are monitoring the exit weirs regularly and making exit weir adjustments as needed and cleaning traveling screens every 4 hours.  This week, the ladder exits were calibrated.  On April 20, the Washington ladder was placed in orifice flow  mode for a short time so an eight-foot long 2x8 plank could be removed from a stationary weir just downstream of the count station.

Fishway Entrances and Collection Channel:  Both ladders met all inspection point criteria this week except for the Oregon ladder south powerhouse pool differential which measured 0.9 feet on April 23.  Collection channel velocities averaged 1.5 feet per second.

Auxiliary Water Supply System:  Fish pump 3 remains out of service due to the oil leak discovered during the last season.  This pump is currently un-watered and repair work is in progress.  Pumps 1 and 2 ran all week with no interruptions in service with blade angles remaining at 30 degrees.  Fish pumps 1 and 2 were respectively taken out of service on April 22 and 23 (15 minutes each) for electrical breaker installations.  The juvenile facility continued to supply the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

The spring bypass season continues with alternating days of primary and secondary bypass with the switch occurring every morning at 0700 hours.  Additional fish samples were taken on April 17, 19, 21, and 23 (primary bypass days) in support of USGS fish tagging activities.  Sample rates during these periods was set at 25% and lasted from 1900 to 2300 hours.  Researchers were not able to collect enough steelhead to meet tagging requirements on April 17 and 19, but were able to meet needs on April 21 and 23.

USGS researchers are utilizing smolts collected from both the regular 24-hour sample and supplemental samples for their study.  For the report week, 43,346 smolts were bypassed during secondary bypass operations.  An additional 2,845 fish were handled in support of USGS research outside of regular sample periods.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains moderate.  Debris distribution and severity is affected by spill and wind conditions.  The number of tumbleweeds appeared to be increasing this week.  Trash rack differentials continued to be monitored and no cleaning was necessary.  No problems were observed within the gatewell slots.

ESBSs/VBSs:  ESBSs are currently deployed in all turbine intake slots.  On April 22, the ESBS in slot 11C was switched to transducer bypass mode due to proximity switch failure.  ESBSs associated with turbine units 1, 2 and 3 were video inspected April 21 and no problems were noted.  The screen in slot 1C was not examined due to a spare ESBS being stored in the slot.  VBS monitoring revealed no problems.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  On April 18, an orifice in slot 5A was found partially obstructed.  The blockage was removed and no harm to fish was noted.  On April 20, a camera was used to examine the opening from the gatewell side of the orifice.  A 5-foot, 2-inch diameter stick with two 12 inch forks was found lodged in the orifice opening.  The general maintenance crew removed the stick and then sealed the orifice so it could be examined.  No other obstructions were found.  All collection channel systems remained in automatic operation.  On April 22, the transition screen cleaning mechanism triggered a timing alarm.  The latch pin was lubricated and the cleaner was returned to service.  Fisheries staff continued to monitor the collection channel, 24 hours/day during primary bypass operations.

Transportation Facility:   Full flow PIT tag detection occurred during primary bypass operations and throughout the facility during secondary bypass operations.  Smolt monitoring only occurred during secondary bypass operations.  The primary (A and B) PIT tag slide gates remained turned off and closed as the return to river lines provide a better bypass route for PIT tagged fish. The secondary (C and D) PIT/bypass gates also remain off and open as there are no studies requiring them this year. Sample gates were functional only during secondary bypass days and during extra collection in support of USGS research.  On April 21, electricians made adjustments to sample tank inflow valve actuators, and mechanics repaired a joint in the B side return to river line.  This line was mostly intact, but had slipped out approximately one inch.  Other than scheduled maintenance, there was nothing else to report this week.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 with clarity data provided by control room.  Temperature, flows and spill data were provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  On April 10 at 0001 hours, spill for juvenile fish passage began with 40 percent of total river flow being spilled.  Spillway gate hoists at bays 1 and 5 underwent testing and maintenance this week.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 257.4 | 221.8 | 104.7 | 89.0 | 48.4 | 46.1 | 4.1 | 2.6 |

*From control room data.

Other

Predatory bird counts continue with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had a high count of 17 gulls, 3 pelicans, 2 cormorants with an occasional tern also being observed.  Occasionally, a gull or pelican would pass near the bypass outfalls.  The water cannon operated well and hazing personnel are on duty.  The high forebay count included 36 grebes with an occasional gull, cormorant, tern or osprey being observed.  One grebe passed into and remained in the collection channel after being observed in gatewell slots.

Invasive Species:  Mussel detectors were checked April 14 and none were found.  The next check will take place approximately May 14.

Inline Cooling Water Strainers:   No cooling water strainers were examined this week.  Annual periodic maintenance for cleaning and inspection will take place in June.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  April 17 – 23, 2009

## Turbine Operation

All turbine units (1 - 6) were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways April 20, 21, and 22.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. No zebra mussels were observed.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.1 feet, off sill with a depth of 8.4 feet, and off sill with a depth of 8.0 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 9.5 feet, off sill with a depth of 9.2 feet, and off sill with a depth of 9.5 feet.  The north shore entrance (NSE) was off sill with a depth of 9.0 feet, off sill with a depth of 10.1 feet, and off sill with a depth of 9.8 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill. All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated.  Seven of 8 south fish pumps were available for operation.  Currently, 6 were operated without problems.  South fish pump 4 is in stand-by and SFP 5 is out of service for gear box repairs.  Repairs to SFP 5 are expected to be completed reporting period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in run mode operation.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.

Removable Spillway Weir:  The RSW is in the operating position.

Fish Sampling:

April 17:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 48 | 2 | 1 | 0 |
| UC-CH | 48 | 0 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 1 | 0 | 0 | 0 |
| UC-SH | 9 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 4 | 1 | 0 | 0 |
| TOTAL | 110 | 3 | 1 | 0 |

April 21:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 71 | 1 | 0 | 0 |
| UC-CH | 68 | 2 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 25 | 0 | 0 | 0 |
| UC-SH | 36 | 1 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 2 | 0 | 0 | 0 |
| TOTAL | 202 | 4 | 0 | 0 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 142.7 | 82.1 | 78.4 | 58.7 | 50 | 47 | 2.7 | 2.4 |

*Unit 1 scrollcase temperature.

Other

Invasive Species: Mussel detectors were checked April 20 and none were found.  The next inspection is scheduled to take place on April 27.

Inline Cooling Water Strainers:  Main turbine unit cooling water strainer screen pressures were checked April 20, 21, and 22.  Pressure differentials were within inspection parameters of “less than or equal to” 4 PSI differential.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  April 17 – 23, 2009

## Turbine Operation

The units are being operated in the 1% operation criteria.

Adult Fish Passage Facility

The adult fishway was inspected by corps or state biologists on April 17, 18, 22, and 23.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections, with the exception of a 7.9’ reading on NPE 1 on April 18 and 7.9 on NPE 2 on April 23.     North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) with on sill depths of 7.4 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections with the exception of a 0.9 foot reading on April 23.

SSE 1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) through this period.  Depth while on sill ranged from 7.6’ to 7.8 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed late in 2009.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 11.0 square yards of forebay debris observed during this period.  A crew was called out to dip gatewells on April 19 when gatewell 2C was found to be over 50% covered.  No oil was observed in gatewells.

STSs/VBSs:  The STS rebuild continues.  STS operation changed to continuous run on April 12 as average fork length of sockeye juveniles was reported as under the 120mm criteria.   STS inspection is scheduled for May 4 and 5.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass is watered up with 20 orifices open.  The mechanical screen cleaner brush lift cable escaped its sheave on April 23 and was out of service until about 1600 hours. The redundant system (bubbler screen cleaner) had no problem maintaining a clean screen.

Collection Facility:  Collection of fish for condition monitoring and avian predation research continued through this period.

Transport Summary:  Not collecting for transport.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 138.8 | 81.7 | 29 | 24 | 48 | 46 | 2.8 | 2.1 |

*Scrollcase temperatures.

#### Other

Invasive Species:  There were no zebra mussels observed at the monitoring stations on April 3.  The next inspection will take place during the first week of May.

Inline Cooling Water Strainers:  The main unit cooling water strainers were cleaned on April 8.  Forty one dead juvenile lampreys were collected from the strainers.  We plan to collect this information monthly through this year.

Project:  Little Goose

# Biologist: Rick Weis

Dates:  April 17 – 23, 2009

## Turbine Operation

Turbine units 1 through 5 were available for service throughout the report period.  Turbine unit 6 remained out of service throughout the week due to isophase bus ground fault errors.  All turbine units were operated within 1% efficiency criteria.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on April 18, 21 and 22.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  All fishway components were in criteria during this report period.  During inspections, channel to tailwater head differentials ranged between 1.50 and 1.54 (criteria 1.0 ft.).  SSE weir depths ranged between 8.25 and 8.28 feet (criteria ≥8.0 ft), NPE weirs rested on or near sill, depths measured between 5.70 and 7.08 feet (criteria ≥7.0 ft. or on sill) and NSE weir depths ranged between 6.06 and 6.24 feet (criteria ≥ 6.0 ft.).  Collection channel water velocities (criteria 1.5 fps) ranged between 2.2 and 3.2 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 1.9 and 2.1 fps.

Auxiliary Water Supply System:  All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Floating forebay debris remained light with up to 60 square feet observed inside the trash/shear boom.

ESBSs/VBSs:  ESBS power panel in slot 6C is out of service and undergoing upgrades and repairs.  All other fishscreens operated within criteria this report period.  Differential measurements were performed on turbine units 1-5 on April 22 and all criteria were met.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 22 open orifices.

Transportation Facility:  Collection continued with 24 hour sample periods and secondary bypass operations.  All components are operating in criteria.  Daily collection for this period ranged between 11,300 and 148,708 for a total of 341,483.   All fish were bypassed to the river except those collected by USGS for researchers.  Descaling and mortality rates for this report period were 0.37% and < 0.1% respectively.

Transport Summary:  Transport operations are expected to begin after May 1.

Spillway Weir:  The spillbay weir was in operation all of this reporting period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 133.6 | 78.5 | 45.8 | 23.8 | 49.2 | 47.2 | 3.0 | 1.9 |

*Ladder temperature.

Other

Invasive Species:  The zebra mussel substrate was inspected on April 6.  No mussels were observed.   The next inspection is scheduled for May 6.

Inline Cooling Water Strainers: Cooling Water Strainers were not checked this week.

USDA – APHIS continued piscivorous bird hazing.  Bird numbers increased this week with a maximum of 13 gulls reported observed during single observation.

USGS researchers continued the juvenile fish passage and survival study with daily tagging and release activities.

Project:  Lower Granite

# Biologist: Mike Halter

Dates:  April 17 – 23, 2009

## Turbine Operation

Lower Granite had turbine units 1 – 6 available for power generation at the beginning of the report week.

## Adult Fish Passage Facility

On April 17, 20, and 21 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings were within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances met criteria during the week with depths ranging between 8.0 feet and 8.1 feet.  Weir depths at the north powerhouse fishway entrances ranged between 6.2 and 6.7 feet during the week due to tailwater elevations below 636.0 feet.  (Whenever tailwater elevations are below 636.0 feet the north powerhouse entrances bottom out and rest on their sills.)  Weir depths at the north shore fishway entrances were out of criteria all week with readings ranging from 5.0 to 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.87 to 1.09 feet per second and averaged 0.95 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.  Bearing repair work continued on fish pump 2 during the week.

#### Juvenile Fish Passage Facility

The facility sample rate was decreased from 1% to 0.5% at 0700 hours on April 19.  Fish were diverted to raceways April 20-22 in support of NMFS PIT-tagging operations (Transport Evaluation and Survival Study).

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was minimal and none was removed this week.  Gatewells are being checked for debris and hand-dipped as circumstances warrant.

ESBSs/VBSs:  There were no ESBS related problems during the week.   ESBS/VBS video inspections are tentatively scheduled for April 24-26.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Nothing to report at this time.

Transportation Facility:  The third transport research barge of the season departed Lower Granite on April 23.  Subsequent trips are planned for every Thursday until normal barging operations begin.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 140.7 | 81.1 | 33.0 | 20.4 | 51.1 | 48.1 | 3.0 | 2.2 |

*Scrollcase temperature.

Other

Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The mussel detector at the head of the adult fishway was checked last week.  The next check is scheduled for early May.

Inline Cooling Water Strainers:   Inline cooling water strainers were last checked during unit annuals.  No evidence of lampreys was found and the cleaners were relatively clear of material.  Strainer checks are to be scheduled in the near future.

Adult fish trap operations continued during the week with a sample rate of 10%.

NMFS continued juvenile fish marking operations for the Transport Study and the Survival Study during the week and began marking for the Extra Mortality Study.  Fish were marked on April 21 and 22 and transported by barge on the morning of April 23.  Fish are being released below Bonneville Dam near Skamania Light.

In addition, fish were also loaded onto the April 23 barge for the Latent Mortality Study (University of Washington).