U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#17-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  June 19 - 25, 2009

## Turbine Operation

McNary had 13 to 14 units available for power generation this week.  Outages this week included turbine unit 13 (returned to service from external thrust bearing oil cooler piping upgrade on June 23), turbine units 8 through 10 (one hour outage for ESBS camera inspection on June 23), turbine unit 6 (8.3 hour outage on June 24 so the hub could be tapped) and turbine unit 5 (3.6 hour outage in support of ESBS replacement in slot B on June 25)..  All turbine units operated within the 1% peak efficiency criterion this week.

## Adult Fish Passage Facilities

McNary fishery biologists performed measured inspections of the adult fishways on June 20, 22, 24 and 25. Visual adult fish counts continued as did temperature monitoring.  Adult lamprey video counts began July 1.

### Fish Ladders:  During measured inspections, both ladders met all Fish Passage Plan criteria.  On June 25, the Oregon tilting weirs received scheduled maintenance.  The Oregon exit’s north traveling screen remains out of service.  The south screen remains in automatic operation and has been functioning well.  Differentials are being monitored with no problems noted.

Fishway Entrances and Collection Channel:  Most Washington ladder inspection points met criteria as did most Oregon ladder inspection points.  Inspection points not meeting criteria included W3 (7.8’ – both W2 and W3 may be out of calibration), SFEW1 (8.5’ to 8.8’ throughout the week), SFEW2 (8.8’ throughout the week) and NFEW2 (8.9’ on June 25).  Collection channel velocities averaged 1.9 feet per second this week.

The flow adjustment for diffuser number 1 mentioned in last week’s report has reduced the number of fish holding in the north powerhouse pool and may have helped to keep the south powerhouse pool differential in criteria for the week.  Powerhouse entrance weir elevations were adjusted and software programs were modified in support of adult lamprey passage tests on June 24.  Calibration for all ladder entrances will be examined and checked in the near future.

Auxiliary Water Supply System: Fish pump 3 remains out of service and unwatered due to the oil leak discovered during the last season.  A contractor successfully repaired the oil leak this week. Project maintenance crews are now repairing a broken equalizing valve. Completion of this work and restoration of pump service is expected in 2 to 3 weeks.  Except for brief outages, pumps 1 and 2 ran all week with blade angles of 30 degrees.  Two outages took place June 25 (1.2 hours total outage time for both pumps) in support of electrical circuit breaker repairs.  The juvenile facility continued to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass operations continued with the switch occurring every morning at 0700 hours.  Approximately 8.6 hours of extra secondary bypass and sampling for USGS tagging activities took place on June 20, 22 and 24 from approximately 2200 to 0200 hours each night at 10 to 25% sample rates.  USGS researchers also utilized fish sampled during regular secondary bypass operations.  For the report week, 377,307 smolts passed through the facility during secondary bypass operations.  An additional 7,551 fish were handled during supplemental sampling periods.  Primary bypass outside the alternating schedule did not occur this week.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris by the powerhouse was moderate.  Trash rack differentials were low and no cleaning was necessary.  Slight oil sheens were seen in 2 gatewell slots during turbine unit outages.  The oil was removed with absorbent pads.  No other problems were observed.

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  Two screens are in transducer bypass mode including screens in slots 11C and 13A.  The third screen previously reported in transducer bypass mode (slot 5B) was replaced on June 25.  ESBS camera inspections took place in turbine units 8, 9 and 10 on June 23.  All screens were found in good condition. The screen in slot 8A slot was not examined as a spare ESBS was stored in that slot.  VBS monitoring efforts revealed no screens out of criteria this week.  On June 23 and 25, a total of 4 VBSs were cleaned as a preventative measure.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were 42 orifices opened and all channel systems operated well in automatic mode.  No debris problems were reported this week except for a stick being removed from an orifice in slot 7B.    Both the side and rectangular screen cleaning mechanism cycle times were set at 120 minutes throughout the week.  Fish facility staff continued to closely monitor the collection channel during VBS cleaning operations and on primary bypass days.

Transportation Facility:  Full spring bypass season continues with alternating days of primary and secondary bypass, returning all fish to the river.  Full flow PIT tag detection takes place during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring only occurs on secondary bypass days.  The primary (A and B) PIT tag slide gates remain off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT tag bypass gates also remain off and open as there are no studies requiring them this year.  The sample gates were active only when the facility was in secondary bypass mode.  Maintenance activities this week included ice blocks checks of the return to the river lines and PIT tag system checks.  Ice block checks removed a small debris blockage from each return to the river line (i.e.: 2 blockages were removed).

Transport Summary:  No transport operations are taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Water clarity data continues to be provided by the control room. The smolt monitoring staff continues gathering water temperature data throughout the project.  This information will be distributed by them in a separate weekly report.

Spill for juvenile fish passage continues with at least 40 percent of flow being spilled.  At 0001 hours on June 20, spill was increased to 50 percent of flow as agreed upon by the region.  All spill adjustments met Fish Passage Plan requirements.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 293.8 | 244.5 | 147.0 | 107.7 | 62.0 | 61.0 | 5.6 | 4.1 |

*From control room data.

Other

Invasive Species:  On June 13, the zebra mussel stations were examined and no mussels were found.  The next inspection is scheduled for approximately July 13.

Inline Cooling Water Strainers:   Cooling water strainers in turbine units 1 through 4, 6 and 8 through 14 were inspected on June 15 and 17.  Strainers associated with turbine units 5 and 7 could not be opened and will be repaired when turbine unit outages can be scheduled.  Thirty juvenile lamprey mortalities and one live juvenile lamprey were recovered from the inspected strainers.

Predatory bird counts continued with the tailwater and forebay areas being checked twice and once a day, respectively.  The tailwater area had high counts of 134 gulls, 44 pelicans, 26 terns and 9 cormorants with an occasional osprey observed.  The high counts at the bypass outfalls were 10 gulls, 5 pelicans and 1 tern.  Pelicans appear to be positioning themselves in areas were they can feed on adult shad.  The highest tailwater counts generally occur during swing shift when hazing personnel are off duty.  The water cannon continued to operate well.  The high forebay count included 17 grebes with an occasional pelican, cormorant, tern or osprey also being noted.  Two additional grebes joined the 4 grebes remaining in the gatewell slots at the end of last week.  One of these birds was removed by APHIS personnel and three passed into the collection channel joining the one bird from last week.  Of the four grebes in the channel, two were removed and one passed out of the system.  This leaves two grebes in the gatewell slots and one in the channel.  No grebes were seen elsewhere.

On June 24, from 0855 to 1238 hours, spill bays 16 to 22 were closed for hydro-acoustic antennae repairs and installation in support of USGS research.  During the outage, 50 percent spill was maintained evenly through the remaining open bays.  Powerhouse flow and dissolved gas levels also met criteria as outlined in the Fish Passage Plan.  The outage lasted 20 minutes longer than expected as TSW2 needed to be closed manually.  Since TSW 1 and 2 gates could not be raised fully out of the water remotely from the control room, local operation of the spillbay hoist and spillbay gantry crane became necessary.  This took an additional 18 minutes.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  June 19 - 25, 2009

## Turbine Operation

Turbine units (1 and 3 through 6) were available for operation this entire reporting period.  Turbine unit 2 went out of service for annual maintenance June 23 at 0755 hours.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways June 22 and 23.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.6 feet on both inspections.  The computer readings for the SFE were all in criteria.  A trouble report to calibrate the south fishway was initiated.  The north powerhouse entrance (NFE) was on sill with a depth of 11.7 feet and on sill with a depth of 14.0 feet.  The north shore entrance (NSE) was off sill with a depth of 9.3 feet and off sill with a depth of 10.4 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill. All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without problem.  North shore fish pump 3 is on standby.  Six of the available 8 south fish pumps were operated without problem.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STSs are in continuous run mode operation.  July STS inspections are scheduled for July 6 and July 13.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.

Removable Spillway Weir:  The RSW is in the operating position.

Fish Sampling:

June 19:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | 3 | 0 | 0 | 0 |
| C-CH-O | 89 | 1 | 0 | 2 |
| UC-CH-O | 76 | 0 | 0 | 1 |
| CH-Fry | --- | --- | --- | --- |
| C-SH | 20 | 1 | 0 | 3 |
| UC-SH | 2 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 190 | 2 | 0 | 6 |

June 23:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 1 | 1 | 0 | 0 |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 87 | 1 | 0 | 0 |
| UC-CH-O | 126 | 0 | 0 | 0 |
| CH-Fry | --- | --- | --- | --- |
| C-SH | 5 | 0 | 0 | 3 |
| UC-SH | 2 | 0 | 0 | 1 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | 4 | 0 | 0 | 0 |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 225 | 2 | 0 | 4 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 109.8 | 82.9 | 62.0 | 28.2 | 60 | 60 | 3.8 | 3.6 |

*Unit 1 scrollcase temperature.

Other

### Invasive Species:  Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found this reporting period.

Inline Cooling Water Strainers: Generator and transformer cooling water strainer’s screen pressures are within clean parameters of < or = 4 PSI differential.  Cooling water strainers are inspected 3 times a reporting period during each adult fishway inspection by fish facility personnel.  All turbine cooling water strainers were cleaned during STS inspections this period.  A total of 8 lampreys mortalities were found in the strainers.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  June 19 - 25, 2009

## Turbine Operation

All turbine units were operated within the 1% operation criteria.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on June 20, 22 and 24.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  When on sill, average depth was 7.5 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE 1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  When on sill, depth was 7.7 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed late in 2009.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 525 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-26% surface coverage.   Gatewell slots were dipped on June 25.  No oil was observed in gatewells.

STSs/VBSs:  STS operation changed to continuous run mode on April 12 as average fork length of sockeye juveniles was reported as under the 120 mm criteria.   STS inspections were conducted June 1 and 2 with all screens found in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass operated with 19 orifices open.  Channel, dewatering structure and flume functioned normally with the exception of the mechanical screen cleaner requiring replacement of the cable spreader sheave on June 23.

Collection Facility:  Fish are being collected for transport.  Equipment is functioning normally.

Transport Summary:  Every other day barging is occurring with barges arriving on odd numbered days.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 106.8 | 80.0 | 25.8 | 17.0 | 61 | 60.5 | 3.3 | 3.0 |

*Scrollcase temperatures.

#### Other

Invasive Species:  There were no zebra mussels observed at the monitoring stations on June 2.  The July inspection will occur some time during the week of July 5.

Inline Cooling Water Strainers: The main unit cooling water strainers were cleaned on June 8.  All fish removed from the strainers were dead with the exception of one juvenile lamprey which was released.  Identified mortalities included: 15 juvenile Chinook, 3 juvenile steelhead, 27 juvenile lamprey, and 45 unidentifiable fish remains.  We plan to collect this information monthly through the year unless water temperature degradation makes this task impossible.

Summer spill began on June 21.

Project:  Little Goose

# Biologists: George Melanson and Rick Weis

Dates:  June 19 - 25, 2009

## Turbine Operation

Turbine units 1 and 3 through 6 were available for service throughout most of this report period.  Turbine unit 2 was returned to service on June 23 at 1348 hours following repairs to the vertical barrier screen (VBS) in slot 2A.  Turbine units 1 through 6 were removed from service for approximately 1 hour each to perform video inspections of ESBSs and VBSs.  Turbine units were operated within 1% efficiency criteria.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on June 19, 21 and 24.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.10 and 1.62 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.20 and 8.26 feet (criteria ≥8.0 ft), NPE weir rested on sill and depths ranged between 5.54 and 6.26 feet (criteria ≥7.0 ft. or on sill) and NSE weir depths ranged between 6.04 and 6.08 feet (criteria ≥ 6.0 ft.).  Collection channel water velocities (criteria 1.5 to 4.0 fps) ranged between 2.3 and 2.7 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.0 and 2.1 fps.

Auxiliary Water Supply System:   All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Floating forebay debris continued to be problematic this report period as debris continued to pass into the gatewells, orifices and collection system.  Inside the trash shear boom debris held steady at approximately 3,000 sq. feet.  Occasional hand removal of debris was performed in several gatewells this report period.  Debris outside the trash shear boom decreased from approximately 6,000 sq. feet to less than 100 sq. feet on June 25.  This debris broke freed of the trash/shear boom and passed over the TSW in spillway 1.

ESBSs/VBSs: ESBS operated within criteria this report period.  To help reduce excess debris loading in the collection channel ESBS cleaning brush sweep cycle times remained at 2-hour intervals.  Video inspections of ESBSs and VBSs were performed from June 23 to June 25.  All screens were observed in good operating condition.  Drawdown inspections on turbine units 1 through 6 were performed on June 25.  All measurements were within criteria.  The trash rack drawdown in slot 1A was measured at 0.5 ft. and was 0.4 feet less than the previous week measurement   (criteria >1.0 ft. from initial reading), allowing removal of the 110 MW operating restriction.  Trash rack cleaning is scheduled to start on June 29.

Orifices, Collection Channel, Dewatering Structure, Flume: The collection channel was operated with 23 open orifices.  The frequency of orifice blockages continued to decrease this report period.   Increased orifices rotations and back flushing continued throughout this report period.

Transportation Facility: Collection and transport continued this report period.  Daily collection ranged between 5,700 and 28,715 for a total of 124,844 for the week.  Descaling and mortality rates for this report period are 0.58% and 0.29% respectively.

Transport Summary: Barging operations took place every other day.  All barge loading and transport operations were performed satisfactorily.

Spillway Weir:  The spillway weir was in low crest operation during all of this reporting period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 103.7 | 78.6 | 31.0 | 23.3 | 60.7 | 60.1 | 3.0 | 2.8 |

*Ladder temperature.

Other

Invasive Species:  The Zebra Mussel substrate was inspected on June 4.  No mussels were observed.   The next inspection is scheduled for July 1.

Inline Cooling Water Strainers: Cooling water strainers were not checked this week.

USDA – APHIS continued piscivorous bird hazing.  On June 22, five gulls were observed during single observations.  No other birds were observed during this report period.

USGS continued juvenile fish passage and survival research.

Project:  Lower Granite

# Biologists: Mike Halter and Casey Watson

Dates:  June 19 - 25, 2009

## Turbine Operation

Lower Granite had turbine units 1 – 6 available for power generation at the beginning of the report week.  Outages took place on June 19 to finish the monthly VBS and ESBS video inspections.  The outage times were as follows: turbine unit 6 (0800 – 1043 hours) and turbine unit 5 (1200 – 1315 hours).  All turbine units were operated within the established guidelines during the report period.

## Adult Fish Passage Facility

On June 19, 20, 23 and 24 the Lower Granite fisheries biologists performed measured inspections of the adult fishway.

Fish Ladder:  Criteria were met with the exception of the water flow over the ladder weirs as measured at the diffuser 14 weir.  The top of the ladder weir is at elevation 727.0 and there should be from 1.0 to 1.3 feet of water over the top of the weir.  On the June 19 and June 20 inspections, the water reading was 727.9 feet - 0.9 feet over the top of the weir and 0.1 feet below criteria.  (The water flow over the ladder weir has been hovering around 727.95 feet – in between rounding to criteria or being just below criteria.)

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at south shore fishway entrances were within criteria on all inspections with the exception of the June 20 inspection when the reading on both gates was 7.9 feet (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were below the 8.0 foot criteria level due to low tailwater elevations which caused the gates to bottom out and rest on their sills.  North powerhouse entrance depths ranged from 6.3 to 7.4 feet during the inspections.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 4.9 and 6.0 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.84 to 1.01 feet per second and averaged 0.90 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.

#### Juvenile Fish Passage Facility

The facility sample rate was increased from 2.0% up to 4.0% at 0700 hours on June 25.

Forebay Debris/Gatewell Debris/Oil:   Debris levels were moderate during the week.  Debris has shifted from fine material to generally more coarse material.

ESBSs/VBSs:  Video camera inspections of the ESBSs and VBSs were completed on June 19.  No additional screen problems were detected.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Collection gallery orifices were back-flushed every three hours during the week.

Transportation Facility:  Every other day fish barge loading continued during the week.  Operations continued to go smoothly.  A considerable amount of debris was removed from the raceways prior to barge loading.

Transport Summary:   Fish were barged on the odd days of the month.   Fish are being picked up for transport at Little Goose and Lower Monumental Dams.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 108.2 | 85.2 | 20.7 | 18.7 | 61.5 | 59.5 | 3.8 | 3.0 |

*Scrollcase temperature.

Summer spill operations at Lower Granite began at 0001 hours on June 21.  Spill is scheduled to take place through August 31 at the rate of 18.6 kcfs/24 hours per day as specified in Table LWG-10 of the 2009 Fish Passage Plan.

Other

Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on June 11.

Inline Cooling Water Strainers:   Inline cooling water strainers were last checked during unit annuals.  No evidence of lampreys was found and the cleaners were relatively clear of material.  Strainer checks are to be scheduled in the near future.

Adult fish trap operations continued during the week.  The sample rate remained at 5%.  Scale samples were taken from both hatchery and wild adult Chinook and tissue samples were also taken from wild Chinook.

The University of Idaho continued radio-tagging subyearling Chinook juveniles to study habitat usage during the week.

University of Idaho/CRIFIC kelt research activities continued during the week.  Steelhead kelt females were diverted into a holding area below the separator for blood work and physiological and endocrinological profiles.