U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#34-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  October 16 – 22, 2009

## Turbine Operation

McNary had 10 to 11 turbine units available for power generation this week.  Turbine units 9 and 10 remain out of service in support of transformer T5 replacement, which should be completed in early November.  Turbine unit 4 remains out of service for 9-year overhaul and is expected to return to service in approximately 2.5 months.  On October 16, turbine units 1, 2, 5, 12 and 13, were out of service a total of 6 hours in support of VBS cleaning operations.  On October 19, 20 and 21, turbine unit 12 and transmission line 6 were taken out of service for a total of 18.4 hours in support of portable crane work on the headgates in turbine units 10 and 11.  Turbine unit 11 returned to service on October 21, following the completion of annual maintenance and headgate adjustments.  All available turbine units operated within the 1% criteria this week.

## Adult Fish Passage Facilities

On October 16, 18 and 21, the McNary fishery biologist performed measured inspections of the adult fishways.  Adult fish counts will cease for the year at the end of October.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  The south traveling screen operated well and continues to supply sufficient water to meet facility needs.  Trash rack and traveling screen differentials remain low and unchanged.  Both exits were checked regularly during storms and no problems were reported.

Fishway Entrances and Collection Channel:  All Washington ladder and nearly all Oregon ladder inspection points met criteria.  SFEW1 was the sole location not meeting criteria this week (weir depth measured 8.6 feet on October 18).  Collection channel velocities averaged 1.7 feet per second.

Auxiliary Water Supply System:   All three fish pumps operated this week with blade angles of 22 to 30 degrees with one problem to report.  On October 21, pump 1 triggered a high water cover plate alarm.  Normal operation resumed after the alarm was reset.    The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service during this report period.

#### Juvenile Fish Passage Facility

Fall primary bypass season continues.

Forebay Debris/Gatewell Debris/Oil: Forebay debris remains light.  Trash rack differentials remained low and no racks were cleaned this week.  Slots at 9B, 9C, 10A, and 10B remain covered in support of T5 transformer replacement.  Slots associated with turbine unit 14 also remain covered in support of main hoist repair work on the intake deck crane.  The covers help keep contaminants from entering the intake slots.  No problems were observed.

ESBSs/VBSs:  ESBSs are currently deployed in at all turbine units.  The screens in slots 9C and 11C slots remain in transducer bypass mode.  No ESBS camera inspections occurred this week, as the majority of fish screens have been recently examined.  Uninspected screens have covered gatewell slots which preclude inspection.  On October 16, two VBSs in turbine unit 1were cleaned.  These screens exhibited high differential readings on October 15.  Five additional screens were also cleaned on October 16 as a preventative measure.  Another VBS was cleaned October 21, after a high differential was measured.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  No problems occurred and all channel systems operated well in automatic mode.  During fall bypass season and VBS cleaning operations, the channel is monitored continuously by technicians.

Transportation Facility: Fall primary bypass season continues.  All systems remain shutdown and light winter maintenance has begun.  The facility remains watered up to avoid frozen pipes should severe weather should arrive before the winter maintenance season.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the control room whose data day runs from 0000 to 2400 hours.  Spillway maintenance continues.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 96.6 | 61.7 | 0.0 | 0.0 | 58.0 | 56.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.

Invasive Species:  On October 11, the zebra mussel stations were examined and no mussels were found.  The next zebra mussel inspection will approximately occur on November 13.

Formal predatory bird counts have ended for the season.  During casual observations, gulls and cormorants were noted feeding and roosting in the tailwater near the powerhouse, with a few birds also being noted at the bypass outfalls.  On October 18, night herons were observed roosting on the barge dock.  Herons were also observed roosting on the barge dock late in the 2008 season.  Grebes were observed in the forebay this week in groups of 8 to 15 individuals.  No grebes were seen elsewhere on site.  Three loons were also noted in the forebay.  The water cannon continued to operate well.  Overall, higher numbers of birds continue to be present this week and most are likely feeding on juvenile shad.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  October 16 – 22, 2009

## Turbine Operation

Turbine unit 4 was out of service for a short period on October 19 while STSs were being inspected.  Turbine units 2 and 3 were also out of service for short periods on October 20 while STS inspections were conducted.  Turbine unit 1 has been out of service out of service for 5-year overhaul since October 1.  Turbine units 5 and 6 went out of service October 3 to facilitate electrical switching and transformer configuration to maintain turbine unit priority.  Turbine units 5 and 6 will remain out of service until the overhaul is completed on turbine unit 1.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways on October 20, 21, and 22.

### Fish Ladders:  All north and south fish ladder inspection points (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.9 feet, on sill with a depth of 7.7 feet, and on sill with a depth of 7.2 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.7 feet, on sill with a depth of 7.7 feet, and on sill with a depth of 7.2 feet.  The north shore entrance (NSE) was off sill with a depth of 7.7 feet, off sill with a depth of 7.0 feet, and on sill with a depth of 7.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The NSE was found with a tripped breaker following the out of criteria events on October 20 and 21.  The operator was notified to correct the problem.  All channel/tailwater differentials were within criteria of 1 – 2 feet.

### Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is in standby status.  Six of the available 8 south fish pumps were operated without problems.  North shore fish pump 3 will be out of service beginning November 2 for an oil leak investigation located around the pump shaft.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  STS’s are in cycle mode operation.  STS inspections for October are now complete.  No problems were found.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: Twenty orifices are open.  The screen cleaner power supply system in the collection channel continues to have problems and is being operated manually once per day.  Other measures included manual operation of the air burst system and manually raking the accessible portions of the inclined screen.  Currently, the project mechanical engineer is designing a new bracket for the power supply.  By lowering the bracket, it should prevent the power supply from being jammed.  In the meantime, the juvenile collection channel water elevations and the incline screen area continue to be monitored regularly by power house operators and fish facility personnel.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.

Removable Spillway Weir:  The weir is in the upright position.  Currently, the weir is not operating as the fish passage spill season has ended.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.5 | 12.2 | 0 | 0 | 62 | 59 | 7.0 | 6.8 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer gages are recorded 3 times a reporting period during each adult fishway inspection by fish facility personnel.  The strainers are being visually inspected during STS inspections.  No lampreys were found during the October inspections.

### Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  October 16 – 22, 2009

## Turbine Operation

All turbine units were operated within the 1% efficiency criteria.  Turbine unit 1 has been out of service since October 1 at 0650 hours for annual maintenance.  Turbine unit 3 was taken out of service from 0816 hours to 1252 hours on October 20 in support of cooling water strainer leak repairs.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or state biologists on October 20, 21, and 22.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  The south shore upper diffuser was adjusted on October 22 to provide a little more water over the weirs.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively).   The trash boom for the north ladder exit was destroyed in a severe wind storm on October 4.  A temporary boom was installed on October 6 and plans are being made to find a weatherproof system to replace it.

### Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were within depth criteria (criteria: > 8’ or on sill) on all inspections.    North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE1 and SPE2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections, with an average depth of 7.6 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

### Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.  Pumps 1 and 2 continued in service throughout this period.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 127 square yards of forebay debris observed during this report period.  Gatewell debris ranged from 0-28% surface coverage.  No oil was observed on project waters.

STSs/VBSs:  STS operation was changed to cycle mode on July 30 as the average fork length of sockeye and chinook juveniles exceeded the 120mm criteria.  October STS inspections were conducted on October 5 and 6.  All were in operable condition. The final STS inspections for 2009 are scheduled for November 2 and 3.  STSs will be raised for winter maintenance on December 16 and 17.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass operated with 18 orifices open.  The new orifice lights have an unusually short operating life which is being investigated.  The channel, dewatering structure, and flume operated normally.

Collection Facility:  The facility switched to primary bypass on October 1 at 0700 hours.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.9 | 13.8 | 0 | 0 | 59.5 | 59 | 5+ | 3.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Turbine unit 1 cooling water strainer was checked on October 13.  There were no debris or fish present.   On October 20, twenty-two juvenile shad mortalities and no debris were removed from the strainers in turbine units 2-6.  This information will be collected monthly through the year unless degradation of fish due to water temperature makes this task impossible.

Invasive Species: There were no zebra mussels observed at the monitoring stations on October 6.  The November inspection is expected to take place during the week of November 2.

Spill gate 4 has been out of service since mid-September for motor repair.  Spill gate 8 was removed from service on October 15.  Bulkheads were installed so the removable spillway weir could be dewatered for viewing by a tour group.

Project:  Little Goose

# Biologist: George Melanson

Dates:  October 16 – 22, 2009

## Turbine Operation

Turbine units 1, 3, and 4 were available for power generation through most of this report period.  Turbine unit 6 was removed from service on September 28 and remains out of service for annual maintenance and SQ-2 panel replacement.  This major electrical panel contains fourteen 480 volt breakers.  Turbine unit 2 was forced out of service on October 1 due to thrust bearing oil pump failure and repairs are in progress.  Turbine unit 5 was removed from service on October 19 at 1347 hours for annual maintenance and 6 year cavitation repair.  All available turbine units operated within 1% efficiency criteria this week.

## Adult Fish Passage Facility

ODFW fishery biologists performed measured inspections of the adult fishway on October 16 and 21.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged from 1.10 to 1.74 ft. (criteria 1.0 to 2.0 ft.).

SSE1 and 2 weir depths ranged from 8.28 to 8.30 feet (criteria ≥8.0 ft).  NPE1 and 2 weir depths ranged between 7.16 and 7.36 feet (criteria ≥7.0 ft. or on sill).  NSE1 depths held steady at 6.12 feet (criteria ≥ 6.0 ft).  NSE2 is raised to approximately 2.5 feet below tail water surface elevation to compensate for water loss through damaged NPE3.

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 3.0 and 3.2 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.1 and 2.4 fps.

Auxiliary Water Supply System:   All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay debris held steady during this report period.  An estimated 2,500 square feet of debris was observed inside the trash-shear boom, mostly in front of turbine unit 1 intakes.  Gatewells for the most part remained clear of debris and contaminants.  A few sticks were removed from gatewell 1A.

ESBSs/VBSs: Manual cycling of the ESBS cleaning brush in slot 1C continued.  All ESBSs were operated within criteria during this report period.

Orifices, Collection Channel, Dewatering Structure, and Flume:  For the most part the collection channel operated with 19 open orifices.  On October 19 from 0700 hours to October 20 at 0730 hours, orifices 5A1 through 5C2 were closed to accommodate headgate installation.  During this time the collection channel operated satisfactorily with 16 open orifices.  The primary dewatering weir motor failed on July 20.  Repairs are on standby - awaiting parts.  The weirs are being manually operated to regulate water flow volume into the bypass flume.

Transportation Facility:   The facility continued collection at 100% sample rates.  A total of 251 salmonid smolts were collected this week.  Descaling was not observed.  Three smolt mortalities were recorded.  All mortalities exhibited symptoms consistent with columnaris disease.

Transport Summary:  Alternate day truck transport operations using the 300-gallon midi-tank continued this week.  Little Goose Dam and Lower Granite Dam continued to conduct joint fish transport operations.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All truck loading and transport activities were performed satisfactorily.

Spillway Weir:  Spillway 1 and the TSW were removed from service on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.1 | 13.0 | 0 | 0 | 59.2 | 58.5 | 6.0 | 4.6 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers associated with turbine units 1 through 6 were inspected on October 21.  One unidentified fish mortality was observed.

Invasive Species:  The zebra mussel substrate was inspected on October 5.  No mussels were observed.   The next inspection is scheduled for November 4.

Up to 24 gulls and 15 cormorants were observed in the vicinity of the dam during the report period.   The increase in bird numbers over the past few weeks is likely a response to the juvenile shad outmigration.

Project:  Lower Granite

# Biologists: Mike Halter and Casey Watson

Dates:  October 16 – 22, 2009

## Turbine Operation

Lower Granite had turbine units 1, 2, 4, 5 and 6 available for power generation at the beginning of the report week.  Turbine unit 3 was returned to available status at 1429 hours on October 22 following annual maintenance.  All operating units were run within the established guidelines.

## Adult Fish Passage Facility

On October 16, 17, 18, and 19 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  An additional inspection was conducted with biologists from the Fish Passage Center and Oregon Department of Fish and Wildlife on October 21.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore entrances ranged between 7.9 and 8.3 feet (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were within the desired 8.0 foot criteria level during all inspections.  North powerhouse entrance weir depths ranged from 8.0 to 8.2 feet.  Weir depth readings at the north shore fishway entrances were out of criteria all week and ranged between 5.0 and 5.2 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.85 to 1.06 feet per second and averaged 0.93 feet per second.

### Auxiliary Water Supply System:  Fish pumps 1 and 3 were run during the week without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels were light during the week.  There were no plugging issues of any kind.

ESBSs/VBSs:  Video inspections are scheduled for October 24-26.  There is a problem with the Lower Granite video camera and arrangements have been made with Little Goose Dam to use their camera for this month’s inspections.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  As a fail-safe measure, collection gallery orifices continued to be backflushed every three hours throughout the week.

Transportation Facility:  The project remained at a 100% sample rate during the week.  Fish were worked up in the lab every other day and transported to the outfall pipe below Bonneville Dam.

Transport Summary:  Lower Granite and Little Goose facilities continued the combined trucking schedule adopted on October 7.  When fish numbers allowed, Lower Granite and Little Goose transported juveniles in one midi-tanker and trucked to Bonneville Dam.  Fish numbers remained low enough this week to allow combined transport on all trips.  This mode of operation is expected to continue until the end of collection. All operations proceeded smoothly.

Removable Spillway Weir:  Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.0 | 13.0 | 0.0 | 0.0 | 59.0 | 57.6 | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 3 were checked for lamprey on September 28.  No evidence of live or dead lamprey was sighted.

Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on September 28.

Adult Fish Trap: Adult fish trap operations continued at a sample rate of 9%.  Trap operations are scheduled to continue until November 15.  A total of 5,000 unclipped (wild) steelhead were scheduled for PIT-tagging by the Idaho Department of Fish and Game.  To date a little over 3,300 steelhead have been tagged.