U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#39-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  November 20 - 26, 2009

## Turbine Operation

McNary had 13 turbine units available for power generation this week.  Turbine unit 4 remains out of service for 9-year overhaul, with an approximate return to service date of December 10.  The soft one percent constraint has been effect since November 1.

## Adult Fish Passage Facilities

On November 21, 23 and 24, McNary fisheries biologists performed measured inspections of the adult fishways.

Fish Ladders:  Both ladder met all Fish Passage Plan criteria during measured inspections except on November 21 when the Oregon ladder head over weir measured 1.5 feet and on November 23 when the Washington ladder head over weir measured 1.4 feet.  Criteria were met in both locations after the weirs were reset by operators. The Washington ladder exit has been in manual mode since November 18.  Biologists and operators will continue to monitor the exits and regulating weirs, making needed adjustments as forebay elevation changes.  The Washington ladder is scheduled to go out of service December 7 for winter maintenance.  The south traveling screen operated well and continues to supply sufficient water to meet facility needs.

Fishway Entrances and Collection Channel: All Washington ladder inspection points met criteria this week.  All Oregon ladder inspection points except SFEW1 also met criteria this week.  SFEW1 measured 8.7 and 8.9 feet, respectively, on November 21 and 23.  Collection channel velocities averaged 1.8 feet per second.

Auxiliary Water Supply System: All three fish pumps operated this week with blade angles of 22 to 30 degrees with no problems to report.  All Oregon ladder diffuser chamber slide gates were tested November 24 for smooth operation and gate positions.  These checks determined whether any gates drifted open or closed during the season.  The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool and the Wasco County PUD unit had no interruptions in service during this report period.

#### Juvenile Fish Passage Facility

Fall primary bypass season continues.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remains light.  No trash racks were cleaned this week as differentials remained low.  Slots 9B, 9C, 10A, 10B, 14A, 14B and 14C remain covered in support of main hoist work on the intake deck crane and for portable crane parking.  The covers help keep contaminants from entering the intake slots.  No problems were observed during this report period.

ESBSs/VBSs:  ESBSs are currently deployed in all turbine units.  The screens in slots 9C and 11C slots remain in transducer bypass mode.  ESBS camera inspections took place in turbine units 6 through 8 this week while these turbine units were in standby mode.  All inspected screens were in satisfactory condition.  Although VBS monitoring revealed no high readings this week, four VBSs (including all 3 in turbine unit 10) were cleaned November 20 as a preventive measure.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: For the week, there were 42 orifices opened.  No problems occurred and all channel systems operated well in automatic mode.  The channel is monitored continuously by technicians during the fall bypass season and during VBS cleaning operations.

Transportation Facility: Fall primary bypass season continues.  All systems remain shutdown and light winter maintenance has begun.  The facility remains watered up to avoid frozen pipes should severe weather should arrive before the winter maintenance season.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the control room whose data day runs from 0000 to 2400 hours.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 112.4 | 84.3 | 0.0 | 0.0 | 50.0 | 48.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.

Invasive Species:  On November 14, the zebra mussel stations were examined and no mussels were found.  The next the zebra mussel inspection will occur approximately on December 14.

Formal predatory bird counts have ended for the season.  During casual observations, gulls, cormorants and mergansers and an occasional grebe were noted feeding and roosting in the tailrace near the powerhouse.  Some birds were also noted at the bypass outfalls.  The water cannon continued to operate satisfactorily.  Only an occasional gull or grebe was observed in forebay locations.  No grebes were observed within the bypass system.  Bird numbers appear to be fluctuating with the juvenile shad out migration.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  November 20 - 26, 2009

## Turbine Operation

Turbine units 2 and 4 were available for operation this entire reporting period.  Turbine unit 3 was briefly unavailable November 23 as the cooling water strainer was being cleaned.  Turbine unit 1 has been out of service for 5-year overhaul since October 1.  Turbine units 5 and 6 went out of service October 3 to facilitate electrical switching and transformer configuration to maintain turbine unit priority and substation stability.  Turbine units 5 and 6 will remain out of service until the overhaul is completed on turbine unit 1.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways on November 20, 23, and 24.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north shore adult fish ladder is tentatively scheduled to be unwatered to tailwater elevation for annual maintenance and inspection January 4 – 15.  Since the floor at the base of this fishway is approximately 5’ below tailwater elevation, complete unwatering is not possible unless bulkheads are installed.  The south shore adult fish ladder is tentatively scheduled to be unwatered completely for annual maintenance and inspection from January 18 to February 26.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.0 feet, on sill with a depth of 7.2 feet, and on sill with a depth of 7.7 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.0 feet, on sill with a depth of 7.2 feet, and on sill with a depth of 7.7 feet.  The north shore entrance (NSE) was on sill with a depth of 7.2 feet, on sill with a depth of 7.1 feet, and on sill with a depth of 7.7 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were within criteria of 1 – 2 feet.

### Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  All 8 south fish pumps are available for operation.  Six of the available 8 south fish pumps were operated without any problems.  North shore fish pump 3 will be out of service beginning December 14 to diagnose and correct a small oil leak thought to be located around the pump shaft.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  STS’s are in cycle mode operation.  STSs are tentatively scheduled to be raised for winter maintenance December 16 – 17.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  The power supply system to the JFF screen cleaner which is located in the juvenile collection channel, continues to have problems.  Due to the hazards of working over the operating juvenile fish channel, permanent repairs will be made when the channel is unwatered this winter maintenance period.

Juvenile Bypass Facility:  The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.  Approximately 270 cfs is dewatered and directed into the south adult fish ladder for adult attraction water leaving 30 cfs for adult fall backs and juvenile fish through the bypass.  The juvenile fish bypass is tentatively scheduled to be unwatered for winter maintenance December 16.

Removable Spillway Weir:  The RSW weir is in the operating position.  Currently, the RSW weir is not in operation due to the end of spill for fish passage.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 20.4 | 13.2 | 0 | 0 | 51 | 50 | 7.2 | 6.6 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer pressures are recorded 3 times a reporting period during each adult fishway inspection performed by fish facility personnel.  On November 23, turbine unit 3 cooling water had low pressure.  The operator was notified and upon investigation, the strainer was found to be plugged with juvenile shad.  The strainer was cleaned and the turbine unit was put back into service.

### Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  November 20 - 26, 2009

## Turbine Operation

All turbine units were operated within the 1% operational criteria.  Turbine unit 3 was taken out of service for annual maintenance on November 2 at 0700 hours and is expected to remain out of service through the month.

Adult Fish Passage Facility

The adult fishway was inspected by Corps’ biologists on November 23, 24 and 25.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively).

### Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were within depth criteria (criteria: > 8’ or on sill) on all inspections.    North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE1 and SPE2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections, with an average on sill depth of 7.4 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

### Auxiliary Water Supply System: AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair, and is “bulkheaded off” to minimize water loss during two-pump operation.  Pumps 1 and 2 continue to operate satisfactorily.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 62.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 - 33% surface coverage.  No oil was observed in the gatewells.

STSs/VBSs: STS operation was changed to cycle mode on July 30 as the average fork length of sockeye and chinook juveniles exceeded the 120mm criteria.  November STS inspections were conducted on November 2 and 3.  The STS in slot 2 C failed the inspection due to missing cross bars.  The damaged screen was replaced the same day.  All other STSs were operable and in satisfactory condition.  STSs will be raised for winter maintenance on December 16 and 17.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass operated with 18 orifices open.  The new orifice lights have an unusually short operating life which is being investigated.  The channel, dewatering structure, and flume operated normally.

Collection Facility:  The facilities were placed in primary bypass mode on October 1 at 0700 hours.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 21.1 | 12.5 | 0 | 0 | 48.5 | 47 | 5+ | 5+ |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Turbine unit cooling water strainers were checked on November 4.  Thirty-seven juvenile shad mortalities were recovered.  No other fish or debris was observed.

Invasive Species: There were no zebra mussels observed at the monitoring stations on November 4.

.

Project:  Little Goose

# Biologist: Rick Weis

Dates:  November 20 - 26, 2009

## Turbine Operation

Turbine units 1, 3, and 4 were available for power generation throughout this report period.  Turbine unit 6 was returned to service on November 20 from annual maintenance and SQ-2 breaker replacement.  Turbine unit 2 was forced out of service on October 1 due to thrust bearing oil pump failure and repairs are in progress.  Turbine unit 5 was removed from service on October 19 at 1347 hours for annual maintenance, 6 year cavitation repair and SQ-2 breaker replacement.  The SQ-2 electrical panel services both turbine units 5 and 6.  All available turbine units operated within 1% efficiency criteria this week.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 23, 24 and 25.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel: Channel to tailwater head differentials ranged from 1.62 to 1.66 feet near the SSE;  1.18 to 1.20 near the NPE1 and 1.08 to 1.12 near the NSE (criteria 1.0 to 2.0 ft.).

SSE1 and 2 weir depths ranged from 8.28 to 8.30 feet (criteria ≥8.0 ft).  NPE1 and 2 weir depths ranged between 6.94 and 7.22 feet (criteria ≥7.0 ft. or on sill).  NSE1 weir broke free after cable and control system failure and is resting on sill at 529.0 ft. (criteria ≥ 6.0 ft).  NSE2 was completely raised and closed off on November 16 at 0940 hours to compensate for water loss through damaged NPE3 and NSE1.

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 2.5 and 3.5 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) measured 2.5 fps on all three inspections.

Auxiliary Water Supply System:    All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remained minimal.  Gatewells for the most part remained clear of debris and contaminants.

ESBSs/VBSs: Manual cycling of the ESBS cleaning brush in slot 1C continued.  All ESBSs were operated within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, and Flume:  The collection channel operated with 19 open orifices.   Power to lights in orifices 5A1 through 6C2 was restored November 20 after SQ-2 breaker replacement was completed and turbine unit 6 was returned to service.

Transportation Facility:  Operations at the facility were switched to primary bypass on October 31.  The water supply/emergency bypass pipe and the facility were dewatered on November 3.  No problems to report – winter maintenance has begun.

Transport Summary:  Transport operations ended October 31.

Spillway Weir:  Spillway 1 and the TSW were removed from service on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 20.3 | 14.4 | 0 | 0 | 47.6 | 46.9 | 6.0+ | 6.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers associated with turbine units 1 through 6 were inspected on October 21.  One unidentified fish mortality was observed.

Invasive Species:  The Zebra Mussel substrate was inspected on November 4.  No mussels were observed.   The next inspection is scheduled for December 2.

Up to 30 gulls and 20 cormorants were observed in the vicinity of the dam during the report period.   The increase in bird numbers over the past several weeks appear to be in response to the juvenile shad outmigration.

Project:  Lower Granite

# Biologist: Mike Halter

Dates:  November 20 - 26, 2009

## Turbine Operation

Lower Granite had turbine units 1, 4, 5 and 6 available for power generation at the beginning of the report week.  Turbine unit 2 returned to available status on November 23 following annual maintenance.  Turbine unit 2 was again taken out of service at 1744 hours on November 25 due to excessive wicket gate packing leakage.  The turbine unit remains off line pending further evaluation.  Turbine unit 3 previously went out of service November 16 after exciter brushes failed.  It is scheduled to return to service by December 31.  All operating turbine units were run within the established 1% guidelines.

## Adult Fish Passage Facility

On November 23, 24, and 25 the Lower Granite fishery biologist performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met during the week.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the November 23-25 inspections.  Weir depths at the south shore entrances were a “mixed bag” this week varying from just out of criteria to just meeting criteria. Weir depths on SSE-1 ranged from 7.8 to 8.0 feet and depths on SSE-2 ranged from 7.9 to 8.0 feet (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse entrances met criteria on all inspections this week and ranged from 8.0 to 8.2. feet (criterion ≥ 8.0 feet). Weir depths at the north shore fishway entrances were below criteria on all inspections this week and ranged from 5.0 to 5.1 feet (criterion ≥ 7.0 feet). Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential. Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.85 to 0.99 feet per second and averaged 0.95 feet per second.

### Auxiliary Water Supply System: Fish pumps 1 and 3 were run during the week without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels were light during the week. There were no plugging issues of any kind.

ESBSs/VBSs:  The last video inspections of the year took place on October 23 and 24.  A small hole was detected on the VBS in slot 1A approximately 3 feet below the surface.  No other problems were detected.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  As a fail-safe measure, collection gallery orifices were back-flushed every three hours throughout the week.  Debris levels remained at very low levels this week.

Transportation Facility:  Fish collection and transportation activities have concluded for the season.  The system was switched to secondary bypass on October 31 with juvenile fish still being routed over the separator for PIT-tag monitoring purposes.  PIT-tag monitoring of juveniles is scheduled to continue until December 15 unless severe winter weather develops and the facility is dewatered to prevent frost damage.

Transport Summary:  Nothing to report as fish transportation activities have concluded for the season.

Removable Spillway Weir:  Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 21.2 | 15.5 | 0.0 | 0.0 | 48.3 | 47.9 | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 3 were checked for lamprey on September 28.  No evidence of live or dead lamprey was sighted.

Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on November 12.

Adult Fish Trap:  Adult fish trap operations were concluded on November 15.  Following testing of the adult trap water supply on November 18, the system was dewatered for the winter season.