U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#40-2009

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  November 27 – December 3, 2009

## Turbine Operation

McNary had 13 turbine units available for power generation this week.  Turbine unit 4 remains out of service for 9-year overhaul, with an approximate return to service date of December 10.  On November 29, ESBSs inspections took place in turbine units 11 and 13, requiring a cumulative total of 39 minutes outage time.    The soft one percent constraint has been effect since November 1.

## Adult Fish Passage Facilities

On November 28, 30 and December 1, the McNary fisheries biologists performed measured inspections of the adult fishways.

Fish Ladders: Both ladders met all Fish Passage Plan criteria during measured inspections except on November 28 when oscillating flow was evident in the Washington ladder and head over weir differentials measured 0.8 feet.  Operators immediately adjusted the weirs and restored normal operation.  The exit will remain in manual operation for electrical upgrades until December 7 when the Washington ladder is scheduled to go out of service for winter maintenance.  Until then, biologists and operators will continue to monitor the exit regularly and make adjustments as forebay elevations change.  On November 29, Oregon exit weir 336 triggered an alarm.  Normal operation resumed after the alarm was reset.  The Oregon exit south traveling screen operated well with no problems observed until December 3 when removal form service became necessary to prevent freeze damage to the spray wash and screen rotation systems.  A dive is scheduled December 7 to insure that the WA ladder dewatering goes well and assist with the north Oregon ladder traveling screen repair.

Fishway Entrances and Collection Channel:  All Washington and most Oregon ladder inspection points were in criteria this week.  Oregon ladder inspection points not meeting criteria included SFEW1 on November 28 (measured 8.9’) and the north pool differential on December 1 (measured 0.9 feet).  The pool differential reading was probably due to the 1000 cfs conduit being closed at the time of the measurement.  Collection channel velocities averaged 1.3 feet per second.

Auxiliary Water Supply System: All three fish pumps operated this week with blade angles of 22 to 30 degrees with no problems to report.  On December 1, the 1000 cfs supply conduit was briefly closed for in support of work at the Oregon exit traveling screens.  The conduit was closed for the season on December 3 to prevent freeze damage.  The juvenile facility continued to supply the usual 450 cfs to the north powerhouse pool until December 3 when the juvenile bypass system was switched from primary to emergency bypass mode.  The Wasco County PUD unit had no interruptions in service this week but will go out of service December 7 when the Washington ladder is to be unwatered.

#### Juvenile Fish Passage Facility

On December 3, primary bypass season concluded with the switch to emergency bypass in anticipation of severe winter weather and for winter maintenance preparation.  The system will remain in emergency bypass until the ESBSs are raised for maintenance in mid to late December, at which time the collection channel orifices will be closed.

Forebay Debris/Gatewell Debris/Oil: Forebay debris remains light.  No trash racks were cleaned this week as differentials remained low.  Slots 9B, 9C, 10A, 10B, 14A, 14B and 14C remain covered in support of main hoist work on the intake deck crane and for portable crane parking.  The covers help keep contaminants from entering the intake slots.  No problems were observed during this report period.

ESBSs/VBSs: ESBSs are currently deployed in all turbine units.  The screens in slots 9C and 11C remain in transducer bypass mode.  ESBS camera inspections took place in turbine units 11 and 13.  All inspected screens were in satisfactory condition.  VBS monitoring revealed no high readings this week, and no VBSs cleanings were necessary.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, there were 42 orifices opened.  No problems occurred and all systems operated well in automatic mode until December 3 when the channel was switched to emergency bypass mode and all equipment (except orifices) was shutdown for the start of winter maintenance.

Transportation Facility:  The facility was completely dewatered and winterized with the start of emergency bypass operations.  Winter maintenance is now in progress.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 with data provided by the control room whose data day runs from 0000 to 2400 hours.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 130.2 | 105.6 | 0.0 | 0.0 | 48.0 | 48.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.

Invasive Species:  On November 14, the zebra mussel stations were examined and no mussels were found.  The next the zebra mussel inspection will occur approximately on December 14.

Formal predatory bird counts have ended for the season.  During casual observations, gulls and cormorants were noted feeding and roosting in the tailrace near the powerhouse.  Some birds were also noted at the bypass outfalls.  The water cannon continued to operate satisfactorily until December 3 when it was taken out of service for the winter.  Only an occasional gull, cormorant or grebe was observed in forebay locations.  No grebes were observed within the bypass system.  Bird numbers appear to be fluctuating with the juvenile shad out migration.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  November 27 – December 3, 2009

## Turbine Operation

Turbine units 2 and 4 were available for operation this entire reporting period.  Turbine unit 1 remains out of service for overhaul.  Turbine units 5 and 6 returned to service December 1 following the end of turbine unit operational priority requirements for fish passage period on November 30.  On December 2, turbine units 3, 5 and 6 were unavailable for short periods to allow cleaning of the cooling water strainers

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways on November 30 and December 1.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north shore adult fish ladder is tentatively scheduled to be unwatered to tailwater elevation for annual maintenance and inspection January 4 – 14.  Since the floor at the base of this fishway is approximately 5’ below tailwater elevation, complete unwatering is not possible unless bulkheads are installed.  The south shore adult fish ladder is tentatively scheduled to be unwatered completely for annual maintenance and inspection from January 19 to February 25.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 6.2 feet and on sill with a depth of 7.2 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 6.2 feet and on sill with a depth of 7.2 feet.  The north shore entrance (NSE) was on sill with a depth of 6.2 feet and on sill with a depth of 7.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were within criteria of 1 – 2 feet.

### Auxiliary Water Supply System:  North shore fish pumps 1 and 2 were operated without any problems.  North shore fish pump 3 is on standby.  All 8 south fish pumps are available for operation.  Six of the available 8 south fish pumps were operated without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  STSs are in cycle mode operation.  Turbine unit 1 STSs were raised December 3.  The remaining STSs are tentatively scheduled to be raised for winter maintenance on December 16 and 17.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe: 20 orifices are open.  The power supply system to the JFF screen cleaner which is located in the juvenile collection channel, continues to have problems. Due to the hazards of working over the operating juvenile fish channel, permanent repairs will be made when the channel is unwatered this winter maintenance period.  The dewatering screen is being monitored and manually cleaned.

Juvenile Bypass Facility: The bypass is in operation with 20 orifices open providing 300 cfs into the juvenile collection channel.  Approximately 270 cfs is dewatered and directed into the south adult fish ladder for adult attraction water leaving 30 cfs for adult fallbacks and juvenile fish being routed through the bypass.  The juvenile fish bypass is tentatively scheduled to be unwatered for winter maintenance December 16.

Removable Spillway Weir:  The RSW weir is in the operating position.  Currently, the RSW weir is not in operation as spill for fish passage ended August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.7 | 14.0 | 0 | 0 | 50 | 47 | 7.2 | 7.2 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Cooling water strainer pressures are recorded 3 times a reporting period during each adult fishway inspection performed by fish facility personnel.  On December 2, turbine units 3, 5, and 6 cooling water strainers were cleaned and put back into service.  Several dead juvenile shad were found.

### Invasive Species: Zebra mussel monitoring devices are inspected by fish facility personnel during the first adult fishway inspection of the reporting period.  No mussels were found during this reporting period.

Fish Salvage: On Monday, November 30, 2 Sturgeon, 25 Channel catfish, and 2 Peamouths were removed from turbine unit 1 draft tube.  All fish were released into the tailrace.  No fish mortalities were observed.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Ken Fone

Dates:  November 27 – December 3, 2009

## Turbine Operation

All available turbine units were operated within the 1% operation criteria.  Turbine unit 3 was previously taken out of service for annual maintenance on November 2 at 0700 hours and remained out of service through this period.  Turbine unit 5 was taken out of service for annual maintenance on November 30 at 0700 hours.

Adult Fish Passage Facility

The adult fishway was inspected by corps biologists on November 30 and December 1 and 3.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively).

### Fishway Entrances and Collection Channel: NPE1 and NPE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections with the exception of the November 30 inspection which had a 7.9” reading.  This would likely have no adverse effect on fish passage.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE1 and SPE2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections, with an average on sill depth of 7.5 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) on all inspections.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 160.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 - 35% surface coverage.  No oil was observed in the gatewells.

STSs/VBSs:  STS operation was changed to cycle mode on July 30 as the average fork length of sockeye and chinook juveniles exceeded the 120mm criteria.  STS inspections were last conducted on November 2 and 3.  The STS in slot 2C failed inspection due to missing cross bars.  The damaged screen was replaced the same day.  All other STSs were operable.  STSs will be raised for winter maintenance on December 16 and 17.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass operated with 18 orifices open.  The new orifice lights have an unusually short operating life which is being investigated.  The channel, dewatering structure, and flume operated normally.

Collection Facility:  The facilities were placed in primary bypass mode on October 1 at 0700 hours.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.2 | 15.1 | 0 | 0 | 46.5 | 45.5 | 5+ | 5+ |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Turbine unit cooling water strainers were checked on December 3.  Fish were not counted as fisheries personnel were unavailable.

Invasive Species: There were no zebra mussels observed at the monitoring stations on November 4.

Due to reports of upcoming freezing weather, the bird aversion sprinklers were shut off on December 3.

.

Project:  Little Goose

# Biologist: Rick Weis

Dates:  November 27 – December 3, 2009

## Turbine Operation

Turbine units 1, 3, and 4 were available for power generation throughout this report period.  Turbine unit 6 was returned to service on November 20 from annual maintenance and SQ-2 breaker replacement.  Turbine unit 2 was forced out of service on October 1 due to thrust bearing oil pump failure and repairs are in progress.  Turbine unit 5 was removed from service on October 19 at 1347 hours for annual maintenance, 6 year cavitation repair and SQ-2 breaker replacement.  The SQ-2 electrical panel services both turbine units 5 and 6.  All available turbine units operated within 1% efficiency criteria this week.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 30 and Dec. 3.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged from 1.54 to 1.62 feet near the SSE; 1.12 to 1.14 feet near the NPE1 and 1.08 to 1.10 feet near the NSE (criteria 1.0 to 2.0 ft.).

SSE1 and 2 weir depths ranged from 8.30 to 8.32 feet (criteria ≥8.0 ft).  NPE1 and 2 weir depths ranged between 7.26 and 7.32 feet (criteria ≥7.0 ft. or on sill).  NSE1 weir previously broke free after cable and control system failure and is resting on sill at 529.0 ft. (criteria ≥ 6.0 ft or on sill).  NSE2 was completely raised and closed off on November 16 at 0940 hours to compensate for water loss through damaged NPE3 and NSE1.

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 3.0 and 3.5 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) ranged between 2.4 and 2.6 (criteria 1.5 to 4.0 fps).

Auxiliary Water Supply System:    All three fish pumps operated within criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remained minimal.  Gatewells for the most part remained clear of debris and contaminants.

ESBSs/VBSs: Manual cycling of the ESBS cleaning brush in slot 1C continued.  All ESBSs were operated within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, and Flume:  The collection channel operated satisfactorily with 19 open orifices.

Transportation Facility:  JFF electrical service was interrupted on Dec.1 from 0830 to 0940 and again on Dec. 2 from 1100 and 1240 for testing of the new Inland Power supply line.

Transport Summary:  Transport operations ended October 31.

Spillway Weir:  Spillway 1 and the TSW were removed from service on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.1 | 14.0 | 0 | 0 | 45.8 | 45.1 | 6.0+ | 6.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers associated with turbine units 1 through 6 were inspected on October 21.  One unidentified fish mortality was observed.

Invasive Species:  The Zebra Mussel substrate was inspected on November 4.  No mussels were observed.   The next inspection is scheduled for December 7.

Up to 30 gulls and 15 cormorants were observed in the vicinity of the dam during the report period.   The increase in bird numbers over the past several weeks appear to be in response to the juvenile shad outmigration.

Project:  Lower Granite

# Biologist: Mike Halter

Dates:  November 27 – December 3, 2009

## Turbine Operation

Lower Granite had turbine units 1, 4, 5 and 6 available for power generation at the beginning of the report week.  Turbine unit 1 was taken out of service on November 27 between 1050 and 1526 hours to correct an electrical ground issue.  Turbine unit 2 was returned to service at 1418 hours on November 30 following leaks and packing repairs.  Turbine unit 3 remained out of service during the week due to failed exciter brushes.  It is scheduled to return to service by December 31.  All operating units were run within the established 1% guidelines.

## Adult Fish Passage Facility

On November 29, December 2, and December 3, the Lower Granite fisheries biologist performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met during the week.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore entrances were within criteria on all inspections with the exception of the November 30 inspection when SSE-1 had a reading of 7.9 feet (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse entrances met criteria on all inspections this week and ranged from 8.0 to 8.2 feet (criterion ≥ 8.0 feet).  Weir depths at the north shore fishway entrances were below criteria on all inspections this week and ranged from 5.0 to 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances continue to be sacrificed in order to maintain the requisite 1.0 foot of head differential. Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.88 to 1.02 feet per second and averaged 0.94 feet per second.

### Auxiliary Water Supply System: Fish pumps 1 and 3 were run during the week without any problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris levels were light during the week. There were no plugging issues of any kind.

ESBSs/VBSs:  The last video inspections of the year took place on October 23 and 24.  A small hole was detected on the VBS in slot 1A approximately 3 feet below the surface.  No other problems were detected.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  As a fail-safe measure, collection gallery orifices were back-flushed every three hours throughout the week.  Debris levels remained at very low levels this week.

Transportation Facility:  Fish collection and transportation activities have concluded for the season.  The system was switched to secondary bypass on October 31 with juvenile fish still being routed over the separator for PIT-tag monitoring purposes.  PIT-tag monitoring of juveniles is scheduled to continue until December 15 unless severe winter weather develops and the facility is dewatered to prevent frost damage.

Transport Summary:  Nothing to report as fish transportation activities have concluded for the season.

Removable Spillway Weir:  Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 22.6 | 14.9 | 0.0 | 0.0 | 46.9 | 46.4 | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:   Inline cooling water strainers on turbine unit 3 were checked for lamprey on September 28.  No evidence of live or dead lamprey was sighted.

Invasive Species:  No evidence of zebra or quagga mussels was found during the week.  The zebra mussel detector at the head of the adult fishway was last checked on November 12.

Adult Fish Trap:  Adult fish trap operations were concluded on November 15.  Following testing of the adult trap water supply on November 18, the system was dewatered for the winter season.