U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#03-2010

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  March 12 – 18, 2010

## Turbine Operation

McNary had 13 to 14 turbine units available for power generation this week.  On March 15, turbine units 4 and 6 were out of service for 1.7 and 6.4 hours respectively for trash rack cleaning.  On March 17, turbine unit 4 was taken out of service for 10.4 hours to permit the exchange of trash racks with turbine unit 6 in support of an upcoming orifice light study.  Turbine unit 6 was taken out of service from March 17 to 18, so the exchange could be completed and allow tapping of the hub.  All turbine units are operating under the soft 1% efficiency constraints.  The hard one percent constraint criteria will begin April 1.

## Adult Fish Passage Facilities

On March 12, 15 and 18, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting is scheduled to resume April 1.  Until then, the picketed leads will remain in their raised positions.

### Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  The north Oregon exit traveling screen remains out of service with repairs possibly commencing next week.  The south Oregon exit traveling screen operated well and differential monitoring revealed no problems.  The Oregon ladder regulating and tilting weirs were examined this week and were found satisfactory.

Fishway Entrances and Collection Channel:  All Washington ladder and most Oregon ladder inspection points were in criteria.  All week on the Oregon ladder, the north powerhouse pool differential measured from 0.8 to 0.9 feet.  North powerhouse pool differentials were likely affected by the juvenile facility not being in service (excess water from juvenile system feeds this adult fishway).  All other Oregon inspection points were in criteria.  Collection channel velocities averaged 1.5 feet per second.

Auxiliary Water Supply System:  For the week, all three fish pumps ran satisfactorily with blade angles of 22 to 30 degrees with except for interruptions in service on March 16.  Vibration tests took place on March 16, from 0807 to 1636 hours.  Fish pump down times were kept to a minimum as all three pumps were intermittently taken out of service.  As mentioned above, the juvenile facility is not yet supplying the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had two interruptions in service on March 18 for total of 1.6 hours outage time.  During the outages, the bypass diverter functioned well.

#### Juvenile Fish Passage Facility

The facility remains shut down for winter maintenance, which is nearly complete.  Primary bypass operations are slated to begin in late March.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris accumulations were light to moderate depending on wind direction.  On March 15, trash rack raking took place at turbine units 4 and 6.  Approximately one ten-yard dump truck load of debris was removed.  Trash rack cleaning should resume next week.  A slight amount of fish screen oil was observed in one slot and subsequently removed with absorbent pads.  No other problems were observed.

ESBSs/VBSs:  ESBS’s remain raised and maintenance is almost complete.  VBS monitoring will resume when fish screen installations begin.  ESBS installations are slated to take place between April 5 and April 15.  As in 2009, ESBSs are being deployed one to two weeks later than previous years as a juvenile lamprey protection measure.  VBS monitoring will resume when fish screen installations begin.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The orifices remain closed for winter maintenance which is nearly finished.  Bypass operations will begin in late March.

Transportation Facility:  The facility remains dewatered for winter maintenance which is nearing completion.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by control room data, which runs from 0000 to 2400 hours each day.  Spillway gate rehabilitation continues.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 109.7 | 85.0 | 0.0 | 0.0 | 43 | 43 | 6.0 | 6.0 |

*Unit 1’s scroll case temperature.

Other

Inline Cooling Water Strainers:  No cooling water strainers were inspected this week.  The next inspection is expected to take place in about a month.

Invasive Species: The zebra mussel stations were inspected March 5, none were found.  The next inspection is expected to take place on April 5.

Bird counts will resume later in the month when technicians arrive for duty.  An occasional gull, or cormorant was observed during ladder inspections.

No researchers are on site at this time.

On March 12 and 13, the USGS pontoon boat mentioned in last week’s report was removed from the river with all oil successfully contained.

River bottom core samples were taken this week.  These cores will help determine the feasibility of potential bypass outfall locations.

Project:  Ice Harbor

# Biologist:  Mark Plummer

# Technician: Stephen Jeffers

Dates:  March 12 – 18, 2010

## Turbine Operation

All turbine units (1 - 6) were available for operation this reporting period.  Turbine unit 1 returned to service March 19 at 1420 hours.  All turbine units were out of service for short periods on March 16 and 17 in support of STS installations.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 15, 16, 17, and 18.

### Fish Ladders: All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria, except on March 16 and 18.   On these inspections, the south upper fish ladder diffuser staff gage indicated 0.9 feet (criteria is 1.0 – 1.3 feet).  The diffuser cannot be operated in automatic mode to adjust for more water.  Maintenance personnel believe the problem is with the diffuser valve.  Valve repair requires unwatering of the upper south adult fish ladder.  Manual operation could cause the valve to fail entirely.  Since adult spring Chinook are expected to arrive in the near future, project personnel decided to leave valve in the current configuration.  The north and south fish ladder picketed leads are currently raised as adult fish counts do not begin until April 1.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 7.4 feet, on sill with a depth of 6.7 feet, on sill with a depth of 6.7 feet, and on sill with a depth of 6.4 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.4 feet, on sill with a depth of 6.7 feet, on sill with a depth of 6.7 feet and on sill with a depth of 6.4 feet.  The north shore entrance (NSE) was on sill with a depth of 7.4 feet, on sill with a depth of 6.6 feet, on sill with a depth of 6.7 feet, and on sill with a depth of 6.4 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All north shore fish pump are in service.  Seven of the 8 south fish pumps are in service.  South fish pump 4 is out of service due to gearbox problems.  On site personnel have finished rebuilding a gear box which should be installed soon.   Since fish pump 4 is out of service, its oil pump was used as a replacement for a faulty oil pump on south fish pump 2.  Another replacement oil pump is being procured.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  STSs were deployed on March 16 and 17.   The STSs are in cycle run timing mode.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put in operation March 8.

Fish Sampling:  The first sample is scheduled for April 5.  Sampling days have changed to Mondays and Thursdays.

Removable Spillway Weir:  The RSW is currently not in operation.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.0 | 20.4 | 0.0 | 0.0 | 44 | 42 | 5.8 | 4.6 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.

Invasive Species:  No zebra mussel inspections were performed this week.

The temporary high velocity experimental separator at Ice Harbor Fish Facility was removed during the winter maintenance season.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Elizabeth Lindsey

Dates:  March 12 – 18, 2010

## Turbine Operation

All turbine units are being operated within the soft 1% operation constraint criteria.  There were no turbine unit outages this week.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on March 15, 16, 17, and 18.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE1 and NSE2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depths readings were two at 7.6, 7.5, and 7.2 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill), with the exception of an out of criteria reading of 7.9 feet on March 18.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and for diffuser assembly repairs.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 42.5 square yards of forebay debris observed during this period.  Debris will be removed from the gatewells and trash racks during the week of March 22.

STSs/VBSs:  STSs were rotated (i..e.: mesh screen motors were operated) on deck for the preseason inspection on March 18.  All were ready for deployment.  Screens will be lowered into position and returned to service during the week of March 22.

Orifices, Collection Channel, Dewatering Structure, Flume:   The bypass will be watered up during the week of March 22.

Collection Facility:  Winter maintenance is nearly completed.  The facility will be watered up for testing the week of March 22.

Transport Summary:  No transport is taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.3 | 17.7 | 0 | 0 | 43.0 | 42.5 | 5.0 | 4.8 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.

Invasive Species: There were no zebra mussels observed at the monitoring stations during the March 9 inspection.

Project:  Little Goose

# Biologist: Richard Weis

Dates:  March 12 – 18, 2010

## Turbine Operation

Turbine units 1 and 3 through 6 were available for service throughout this report period.  Turbine unit 2 was removed from service on March 4 at 1600 hours due to field grounding errors.  All turbine units were operated within the soft 1% efficiency constraint criteria.

## Adult Fish Passage Facility

USACE fisheries biologists performed measured inspections of the adult fishway on March 15, 16 and 18.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Most fishway measurements were in criteria during inspections.  Channel to tailwater head differentials ranged between 1.22 and 1.56 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.34 and 8.68 feet (criteria ≥8.0 ft), NPE1 weir is manually positioned on sill and depths measured between 7.24 and 7.44 feet (criteria ≥7.0 ft.). NPE2 weir depths ranged between 7.20 and 7.30 feet (criteria ≥7.0 ft.).  NSE1 is manually positioned at 532.5 feet and depths measured between 6.50 and 6.78 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.16 and 6.22 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.5 and 1.7 fps near the SSE and 2.0 to 2.8 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 1.1 and 1.2 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 20,000 square feet of floating debris remained inside the trash-shear boom.  Another 3,500 square feet was observed outside the trash-shear boom.

Spillway Weir:  The spillway weir was not in service during this report period.

ESBS/VBS:  All ESBS remained raised in their winter storage positions.  Maintenance continues.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system is out of service for winter maintenance.

Transportation Facility:  The facility is out of service for winter maintenance.

Transport Summary:  Transport operations are expected to begin in April.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.7 | 17.2 | 0 | 0 | 43.7 | 42.0 | 6.0+ | 6.0 |

*Ladder temperature.

Other

Cooling Water Strainers:  Cooling water strainers for all 6 turbine units were inspected on March 9.  Two juvenile lamprey mortalities were collected from unit 3 strainers.  No other fish or fish remains were observed.  The next inspection of the cooling water strainers is scheduled for April 7.

Invasive Species:  The Zebra Mussel substrate monitor is scheduled for inspection on April 5.

Avian Activity: An occasional gull was observed during this report period.

HARCON, Inc. contractor work continued on the primary dewaterer, downwell, diversion valves, and outfall flume/pipe.  All of these new or modified structures successfully completed operational tests on March 8.  Completion is expected March 23.

Project:  Lower Granite

# Biologist: Mike Halter

Dates:  March 12 – 18, 2010

## Turbine Operation

Lower Granite had turbine units 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 1 was returned to service at 1700 hours on March 17 following thrust bearing repairs.  Turbine unit 3 remains out of service for a rewind and will not be available until approximately December of 2010.

## Adult Fish Passage Facility

On March 15 and 17 the Lower Granite fisheries biologist performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings were within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at both south shore fishway entrances were within criteria on the March 17 inspection but slightly out of criteria on the March 15 inspection with readings of 7.9 feet on each entrance (criterion ≥ 8.0 feet).  Weir depths at the north powerhouse fishway entrances were out of criteria on both inspections this week with depths ranging between 7.1 and 7.7 feet (criteria ≥ 8.0 feet).  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 5.0 and 5.1 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.92 to 1.02 feet per second and averaged 0.97 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

The juvenile fish collection/bypass gallery was watered up on the morning of March 18.  The separator was placed in primary bypass mode at that time and will continue to operate in this manner until the start of sampling activities on March 25.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was minimal and none was removed this week.  Trash was raked from all turbine units in late February.

ESBSs/VBSs: ESBSs remained dogged off during the report week.  ESBS inspections were conducted on March 15 to make sure they were in good condition prior to deployment.  All screens appeared to be fully operable and ready for use this season.  Deployment of ESBSs is scheduled to begin on March 19.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The collection channel was watered up on the morning of March 18.  The north orifice in each bulkhead slot is being operated for fish passage.  In addition, six fish screen slot orifices (B slots) are also being operated.

Transportation Facility:  General transport operation plans are uncertain at this time but could start earlier than recent years due to the low flow forecast.  The first research barge is slated to leave Lower Granite on April 8.  Juvenile fish sampling (only) activities are tentatively scheduled to begin on March 25.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk – feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.6 | 17.6 | 0.5 | 0.0 | 44° | 44º | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Cooling Water Strainers:  The next inspection of the cooling water strainers is scheduled for March 15.

Invasive Species:  No report.

Video counts in the adult fish ladder counting room began on March 1.  The recording hours are from 0600 to 1600 hours.

Adult fish trap operations resumed on March 1 with a sample rate of 15%.  Wild steelhead are being PIT-tagged and genetic and scale samples are being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead.