U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#09-2010

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  April 23 - 29, 2010

## Turbine Operation

McNary had 12 turbine units available for power generation this week.  Turbine units 2 and 7 are scheduled to return to service on April 30.  On April 28, turbine unit priority was changed to insure units 4, 5 and 6 would be available for upcoming fisheries research.  No turbine units operated outside the 1% efficiency criterion this week.

## Adult Fish Passage Facilities

On April 23, 25, 27 and 29, McNary fisheries biologists performed measured inspections of the adult fishways.  Adult fish counts continued.

### Fish Ladders:  Both ladders met all Fish Passage Plan criteria during inspections.  The Washington ladder regulating weir triggered an alarm once this week.  Normal operation resumed after the alarm was reset.  The Oregon tilting weir 337 also triggered one alarm this week.  Normal operation resumed after the alarm was reset.  The Oregon exit traveling screen operations were satisfactory this week as were screen differentials.

Fishway Entrances and Collection Channel:  All inspection points were in criteria for both the Washington and Oregon fishways.  All entrance weirs performed well even with the hydraulic gradients being produced by the spill program.  Collection channel velocities averaged 1.3 feet per second.

Auxiliary Water Supply System:  All fish pumps ran satisfactorily with blade angles of approximately 28 degrees except for fish pump 2 which had with two interruptions in service.  On April 28, pump 2 was out of service twice to repair a serious packing leak which was flooding the pit area.  Outage time totaled 1 hour.  The juvenile facility continues to add 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service during this report period.

#### Juvenile Fish Passage Facility

Alternate days of primary and secondary bypass operations continued, with the switch between bypass modes occurring each morning at 0700 hours.  No deviations from this schedule occurred this week.  For this report period, 71,822 smolts were routed to the tailrace during secondary bypass operations.  Extra sampling and smolt collection on primary bypass days (twice per week) is now slated to begin May 3.  This work in support of research was previously scheduled to begin April 27.

Forebay Debris/Gate well Debris/Oil:  Forebay debris accumulations were light.  Wind has been dispersing incoming floating debris.  Trash rack cleaning will resume April 30.  No problems were observed in the gatewell slots.

ESBSs/VBSs: ESBSs are currently deployed in all turbine units except for those in turbine unit 7.  These screens will be installed on April 30.  Turbine unit 2 ESBSs installations took place on April 29.  Turbine unit 2 remains out of service due to a control problem in one of the newly installed screens.  Screens in slots 5C, 9A and 9C remain in transducer bypass mode.  On April 24, a screen in slot 10C was found to be cycling too often.  Normal operation resumed after cycling times and limits were adjusted and reset.  On April 27, the ESBS in slot 11B triggered an alarm and would not reset.  Closer examination revealed an electrical problem with the screen controller.  Normal operation resumed after electricians completed repairs.  ESBS camera inspections will begin in May.  VBS differential monitoring efforts revealed no unusual readings this week and no cleaning operations were necessary.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 42 orifices were in use and no obstructions were noted.  All systems operated well this week in automatic mode.  Maintenance activity included south orifice lubrication in slot 8C to improve smoothness of blade movement, and the replacement of the fish attraction light fixture in orifice 2B.  Fisheries staff continues to monitor the collection channel during all shifts when primary bypass operations are taking place.

Transportation Facility:  Spring bypass season continued with alternating days of primary and secondary bypass.  All sampled fish were returned to the river.  PIT tag detection occurs in the full flow pipe during primary bypass mode and throughout the facility during secondary bypass operations.  Smolt monitoring occurs only during secondary bypass days.  Primary (A and B) PIT tag slide gates remained off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The PIT tag system underwent scheduled maintenance this week without incident.  Sample gates continued to function well.  Ice block checks of the return to river lines indicated no blockages this week.  On April 26, high water levels were observed in the separator following the transfer of electrical load generation between turbine units.  High water conditions persisted for 10 minutes.  The collection channel and other parts of the fish facility did not appear to be affected.   A raised tailscreen was discovered in a raceway holding sample fish on April 27.  These fish were being held for recovery following anesthetization and examination.  The tail screens apparently were left slightly raised (6” – 8”) following the previous release of sample fish 2 days earlier.  No fish losses were observed, and sample fish were released as usual following the prescribed recovery period.  Corps and SMP personnel reviewed raceway loading, holding and release procedures following this incident.

Transport Summary:  No fish transport is taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  The spring spill program continues with 40 percent of the river discharge being spilled.  Because of low river flows, spill patterns were adjusted for brief periods to allow towboats and barges safe entrance into and egression out of the navigation lock.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 187.3 | 165.7 | 75.1 | 66.7 | 51.9 | 50.7 | 5.3 | 4.8 |

*Control room data.

Other

Inline Cooling Water Strainers:  The next approximate strainer cleaning date will be May 12.

Invasive Species: The zebra mussel detection stations were last inspected April 5, none were found.  The next examination of the zebra mussel stations will take place May 1.

Predatory bird counts continued with tailwater and forebay observations conducted twice and once daily, respectively.  The tailwater high counts included 43 gulls, 6 pelicans with an occasional cormorant being noted.  Most tailwater birds were seen in the spill area.  Only one gull was seen passing near the bypass outfalls.  Forebay area high counts included 100 grebes with an occasional gull, pelican or osprey being noted.  Three grebes were noticed in the gatewell slots this week.  Of these, one passed into the collection channel and out of the system, leaving two grebes in the slots.  The water cannon continued to operate well.  APHIS bird hazing personnel are on duty seven days a week.

Preparations for the orifice light and unit load studies are almost completed and both studies should begin next week.

GBT monitoring continued.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Dates:  April 23 - 29, 2010

## Turbine Operation

All turbine units (1 - 6) were available for operation during this reporting period.  Turbine unit 1 was out of service from April 25 (0508 hours) to April 26 (0750 hours).  During this outage, turbine unit 2 was operated as the priority turbine unit.  A teletype was issued April 25 at 0846 hours clarifying Fish Passage Plan turbine Priority when turbine unit 1 is out of service.  Turbine unit 3 was out of service April 26 from 0947 hours until 1234 hours.  No other problems to report.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways April 23, 26, 27, 28, and 29.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.4 feet, off sill with a depth of 7.5 feet, off sill with a depth of 7.4 feet, off sill with a depth of 7.5 feet, and off sill with a depth of 8.9 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 12.0 feet, on sill with a depth of 9.2 feet, on sill with a depth of 9.0 feet, on sill with 9.5 feet, and off sill with 8.1 feet. The north shore entrance (NSE) was off sill with a depth of 8.4 feet, on sill with a depth of 6.2 feet, on sill with a depth of 9.0 feet, on sill with 9.5 feet, and on sill with 6.7 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria, except at the NSE.  On the April 23, 26, and 27 inspections, the channel/tailwater differential was 2.1 feet, 2.5 feet, and 2.5 feet respectively.  This condition was due to the fish entrance being on sill.  The weir could not be lowered to reduce the head differential. Channel/tailwater differential criteria are 1 – 2 feet.  Spill is making visual staff gage reading difficult due to rapid changes in water elevation at the staff gage.  Computer readings indicate the fishways are in criteria.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All north shore fish pump are in service.   Six of the available 8 south fish pumps were operated.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STSs are in cycle run timing mode.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was placed into operation March 8.

Juvenile Fish Sampling:  Sampling days has changed to Monday and Thursday.

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:

April 26:

| Species | Sampled | #Descaled | Mortalities | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 16 | 0 | 0 | 0 |
| UC-CH | 19 | 1 | 1 | 1 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 80 | 0 | 1 | 0 |
| UC-SH | 14 | 1 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 129 | 4 | 2 | 1 |

April 29:

| Species | Sampled | #Descaled | Mortalities | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 22 | 0 | 0 | 0 |
| UC-CH | 17 | 0 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 98 | 2 | 0 | 1 |
| UC-SH | 11 | 0 | 0 | 3 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 148 | 2 | 0 | 4 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 75.4 | 53.8 | 49.4 | 43.8 | 50 | 47 | 5.4 | 4.5 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Turbine unit cooling water strainers inspections were last completed April 2.  No lampreys were found.

Invasive Species: No zebra mussels were observed during the April 26 inspection.

Spill for fish passage began April 3.

Project:  Lower Monumental Dam

# Biologists:  Bill Spurgeon and Elizabeth Lindsey

Dates:  April 23 - 29, 2010

## Turbine Operation

All turbine units operated within the hard 1% operational constraint criteria.  There were no turbine unit outages during this week.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on April 23, 24, 25, and 28.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.4’, 7.0’, 6.6’, and 5.6 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.9’, 7.6’, 6.9’, and 5.8 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System:  AWS pump 3 remains out of service for bearing housing replacement and diffuser assembly repair.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was no forebay debris observed during this period.  Gatewell debris ranged from 0-25% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STSs are operating in cycle mode.

Orifices, Collection Channel, Dewatering Structure, Flume:  The bypass is watered up with 19 orifices open.

Collection Facility:  The facility is watered up and ready for fish collection and transport.  Collection of fish for condition monitoring began on April 1.  Subsequent collection for condition monitoring is taking place every third day from 0400 to 1200 hours.

Transport Summary:  Not collecting for transport at this time.  Fish transport operations at Lower Monumental are to begin on May 5.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 73.6 | 52.7 | 26.9 | 23.9 | 53.0 | 51.0 | 4.2 | 3.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Turbine unit cooling water strainers were last cleaned on April 12.  Three lamprey mortalities were recovered.

Invasive Species: There were no zebra mussels observed at the monitoring stations on the April 11 inspection.

Spring spill operation was initiated at 0001 hours on April 3.

Project:  Little Goose

# Biologists: George Melanson and Richard Weis

Dates:  April 23 - 29, 2010

## Turbine Operation

All turbine units were available for service with the following exceptions.  Unit 3 was forced out of service April 23 at 1001 hours due to failed brush motor on ESBS 3A.  Unit 3 was returned to service April 27 at 0850 hours following repairs.  Unit 5 was forced out of service on April 24 at 0617 hours due to an oil leak on the servo-gate, gate lock line.  Repairs were made and unit 5 was returned to service April 27 at 1645 hours. All turbine units were removed from service for up to 2 hours each to conduct video inspections of ESBS and VBS.  All turbine units were operated within 1% of best efficiency.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway April 23, 26 and 28.

Fish Ladder:  The ladder exit head differentials measured between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged from 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at all fish entrances ranged between 1.16 and 1.76 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.20 and 8.36 feet (criteria ≥8.0 ft), NPE weirs rested on sill position and depths ranged between 5.16 and 5.58 (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 8.18 and 8.76 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.12 and 6.24 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.6 and 2.1 fps near the SSE and 2.2 to 2.8 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.7 and 1.0 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Debris inside the trash-sheer boom ranged from 0 to 100 square feet.   Gatewells remain clear of debris and oil.

Spillway Weir:  The weir is positioned in the high crest (622 ft.) spilling approximately 7,200 cfs.

ESBS/VBS:   ESBS 3A cleaning brush was observed not working on April 23 and could not be restarted.  The screen was raised on April 26 and repairs were performed.  The screen was lowered back into position on April 27 and returned to service at 08850 hours.   All other operating ESBS were within criteria this report period.  Video inspections were performed on all ESBS and VBS except 2B and 2C this week.  All screens inspected were observed in good condition and proper operating order.   Drawdowns measurements across trash racks and ESBS/VBS associated with turbine units 1 through 3 were conducted on April 29.  All criteria were met.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel is operating with 21 open orifices.

Transportation Facility:  The juvenile fish collection and transportation facility switched from primary bypass on April 25 at 0700 hours to April 26 at 0700 hours to perform limited condition sampling.  A total of 642 smolts were collected.  Fish sampled were determined to be in good condition.  After this 24 hour sample the facility was placed back into primary by-pass.  Direct loading operations are to begin at Little Goose on May 1 with the first scheduled barge departure on May 2.

Transport Summary:  Collection for transport is scheduled to start May 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 74.7 | 51.4 | 22.3 | 15.4 | 54.0 | 52.7 | 5.0 | 4.0 |

*Ladder temperature.

Other

Invasive Species:  The Zebra Mussel substrate monitor was inspected on April 30, no mussels were observed.  The next inspection for zebra mussels is scheduled for May 23.

Cooling Water Strainers:  Cooling water strainers were inspected on April 27.  No fish were found.

Avian Activity:  :  USDA – APHIS commenced piscivorous bird hazing on April 16.  Up to 13 gulls and 6 Cormorants were observed during a given day during this report period.

Project:  Lower Granite

# Biologist: Mike Halter and Ches Brooks

Dates:  April 23 - 29, 2010

## Turbine Operation

Lower Granite had turbine units 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 1 was returned to service at 1051 hours on May 3.  Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.

## Adult Fish Passage Facility

On May 1, 2, and 4 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met with the exception of the ladder weir differential at diffuser 14 which was 0.9 feet (0.1 feet below criteria) on the May 4 inspection (criterion 1.0 – 1.3 feet).

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were within criteria this week as tailwater elevations were above 633.0 feet.  North powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet.  Weir depths at the north powerhouse entrances ranged from 5.5 to 5.8 feet.  Weir depths at the north shore fishway entrances were out of critieria all week with readings of between 4.9 and 5.2 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.89 to 1.07 feet per second and averaged 0.99 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

The sample rate remained at 0.5% during the report week.  Fish numbers have been relatively low for this time of year but still high enough to merit the low sample rate.

Forebay Debris/Gatewell Debris/Oil:  Debris accumulation in the forebay and gatewells was minimal during the week.   It was not necessary to hand-dip debris from any gatewells this week.

ESBSs/VBSs:   There were no problems with fish screens during the report week.  The next ESBS/VBS inspections are scheduled for May 21-23.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being back-flushed every three hours around the clock to ensure they remain free of obstructions that might impede fish passage.

Transportation Facility: All aspects of facility operation at Lower Granite have been proceeding smoothly.

Transport Summary:  Every day barge departures at Lower Granite began on April 26.  Direct loading operations are to begin at Little Goose on May 1 with the first scheduled barge departure on May 2.  Fish transport operations at Lower Monumental are to begin on May 5.

Removable Spillway Weir:   The RSW is in service.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 65.7 | 52.8 | 20.6 | 20.3 | 52.4 | 50.5 | 3.8 | 3.0 |

*Scrollcase temperature.

Other

Invasive Species:   The zebra mussel trap at the adult fishway exit was last examined for zebra mussels on the April 12 inspection.  No evidence of zebra mussels was found.

Cooling Water Strainers:  The last inspection of the inline cooling water strainers took place on April 15.  The next inspection is scheduled for mid-May.

Research:  The University of Idaho continued steelhead kelt research work at the recently constructed holding tanks upstream of the main fish facility.   Steelhead kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts were sampled for blood, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river during the report week.   Steelhead kelts are now being barged on Wednesdays.

NOAA-Fisheries personnel tagged fish for the survival study, the extra mortality study, and the transport study at the marking facility during the week.  All transport study smolts and roughly half from the extra mortality study smolts were barged and released below Bonneville Dam.

PNNL personnel continued to mark and acoustically tag fish in support of the Survival and Behavior Study. Released fish will be tracked through the Columbia River Estuary.   This study will examine the migratory behavior and ocean-entry timing of both stream and ocean type juvenile Chinook through the lower Columbia River, the estuary and the river plume egression in the ocean.

Idaho Department of Fish and Game personnel conducted genetic stock identification work on Chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of spring/summer Chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  Sampling is taking place every day with a goal of collecting between 2,500 and 4000 genetic samples from both Chinook and steelhead.

The adult fish trap operated at a 4% sample rate during the week.  Wild steelhead are being PIT-tagged with genetic and scale samples also being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead.  One out of every seven hatchery Chinook are being PIT-tagged.  Scale samples and genetic materials are also being taken from the PIT-tagged adult Chinook.

Two sort-by-code projects are also under way:  1) up to 15 Lemhi-origin Chinook are to be diverted for radio-tagging,   2) Chinook that were acoustic-tagged in the estuary are being diverted to check the recovery status of acoustic tag implant surgery and take reference photos.